## Cover
BOTB (PKG-1) PROJECT
July. 01, 2026
| 기안 | 팀장 | 실장
본 문서의 내용과 관련된 지적재산권에 대한 소유는 현대엔지니어링에 있으며 본문서의 내용에 대한 무단복제 및 무단도용은 법에 저촉됨을 알려 드립니다. Intellectual property right of this document is belongs to Hyundai Engineering. Any reproduction and copy without permission of Hyundai Engineering will be strongly prohibited.

## Cable
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Core/Pair Number | Composition | Conductor Size | Earthing Size | Unit of Cable Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [10 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[18 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | C |  | Cable |  |  |  |  | 0 |  | 0 | 0
2 | Valid |  | C.16 |  | POWER, FLAME RETARDANT, ARMORED |  |  |  |  | 0 |  | 0 | 0
3 | Valid |  |  |  |  | AC POWER CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
4 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
5 | Valid |  |  |  |  | Steel Wired Armored |  |  |  | 0 |  | 0 | 0
6 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
7 | Valid |  |  |  |  | Conductor Color : Black(Live), White(Neutral), Green/Yellow tracer(Ground) |  |  |  | 0 |  | 0 | 0
8 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
9 | Valid |  |  |  |  | Jacket Material and Color : PVC, BLACK |  |  |  | 0 |  | 0 | 0
10 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
11 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
12 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
13 | Valid |  | C.16.1 |  |  |  | 3 x C x 12 AWG | FL, PW, SWA | EC01AC05AK99AF01AA99ZZ99 | 3 | C | 12 | 0 | AWG | M285711381A | M | 15800 |  |  | 15800
14 | Valid |  | C.16.1.1 |  |  |  | 3 x C x 12 AWG | TE, PW, SWA |  | 3 | C | 12 | 0 | AWG |  | M | 0
15 | Valid |  | C.16.2 |  |  |  | 3 x C x 10 AWG | FL, PW, SWA | EC01AC05AK99AF01AA99ZZ99 | 3 | C | 10 | 0 | AWG | M367485413A | M | 0
16 | Valid |  | C.16.3 |  |  |  | 3 x C x 2 AWG | TE, PW, SWA |  | 3 | C | 2 | 0 | AWG |  | M | 0
17 | Valid |  | C.16.4 |  |  |  | 3 x C x 6 AWG | TE, PW, SWA |  | 3 | C | 8 | 0 | AWG |  | M | 1000 |  |  | 1000
|  |  | C.16.5 |  |  |  | 2 x C x 14 AWG | FL, PW
18 | Valid |  | C.17 |  | POWER, FLAME RETARDANT, NON-ARMORED |  |  |  |  | 0 |  | 0 | 0
19 | Valid |  |  |  |  | AC POWER CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
20 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
21 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
22 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
23 | Valid |  |  |  |  | Conductor Color : Black(Live), White(Neutral), Green/Yellow tracer(Ground) |  |  |  | 0 |  | 0 | 0
24 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
25 | Valid |  |  |  |  | Jacket Material and Color : PVC, BLACK |  |  |  | 0 |  | 0 | 0
26 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
27 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
28 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
29 | Valid |  | C.17.1 |  |  |  | 3 x C x 14 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 14 | 0 | AWG | M285711330A | M | 0
30 | Valid |  | C.17.2 |  |  |  | 3 x C x 12 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 12 | 0 | AWG | M285711328A | M | 2400 | [6 empty] | 900 | 600 |  |  | 900
31 | Valid |  | C.17.2.1 |  |  |  | 3 X C X 12 AWG | FL, PW, TE |  | 3 | C | 12 | 0 | AWG |  | M | 0
32 | Valid |  | C.17.3 |  |  |  | 3 x C x 10 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 10 | 0 | AWG | M285711329A | M | 0
33 | Valid |  | C.17.4 |  |  |  | 3 x C x 8 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 8 | 0 | AWG | M414586702A | M | 0
34 | Valid |  | C.17.5 |  |  |  | 3 x C x 6 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 6 | 0 | AWG | M414586703A | M | 2600 | [6 empty] | 600 | 1400 |  |  | 600
35 | Valid |  | C.17.6 |  |  |  | 2 x C x 14 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 2 | C | 14 | 0 | AWG | M285711331A | M | 2400 | [6 empty] | 900 | 600 |  |  | 900
36 | Valid |  | C.18 |  | GROUNDING CABLE, FLAME RETARDANT |  |  |  |  | 0 |  | 0 | 0
37 | Valid |  |  |  |  | GROUNDING CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
38 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
39 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
40 | Valid |  |  |  |  | PVC insulated |  |  |  | 0 |  | 0 | 0
41 | Valid |  |  |  |  | Jacket Material and Color : EXTRUDED PVC, COLOR GREEN/YELLOW |  |  |  | 0 |  | 0 | 0
42 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
43 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
44 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
45 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
46 | Valid |  | C.18.1 |  |  |  | 1 x C x 10 AWG | FL, GR/YE | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 10 | 0 | AWG | M285711385C | M | 5895 |  |  | 5520 |  |  |  | 110 | 125 |  |  | 140
47 | Valid |  | C.18.2 |  |  |  | 1 x C x 2 AWG | FL, GR/YE | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 2 | 0 | AWG | M285711541C | M | 25440 |  |  | 25040 |  |  |  | 80 | 240 |  |  | 80
48 | Valid |  | C.18.3 |  |  |  | 1 x C x 2 AWG | FL, GR/YE, TE |  | 1 | C | 2 | 0 | AWG |  | M | 0
49 | Valid |  |  |  |  | GROUNDING CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
50 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
51 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
52 | Valid |  |  |  |  | PVC insulated |  |  |  | 0 |  | 0 | 0
53 | Valid |  |  |  |  | Jacket Material and Color : EXTRUDED PVC, COLOR GREEN |  |  |  | 0 |  | 0 | 0
54 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
55 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
56 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
57 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
58 | Valid |  | C.18.4 |  |  |  | 1 x C x 6 AWG | FL, GR | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 6 | 0 | AWG | M368405088A | M | 0
59 | Valid |  | C.18.5 |  |  |  | 1 x C x 6 AWG | FL, GR, TE |  | 1 | C | 6 | 0 | AWG |  | M | 0
60 | Valid |  | C.18.6 |  |  |  | 1 x C x 2 AWG | FL, GR | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 2 | 0 | AWG | M285711541D | M | 0
61 | Valid |  | C.19 |  | FIBER OPTIC, FLAME RETARDANT, AMOURED, OUTDOOR |  |  |  |  | 0 |  | 0 | 0
62 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
63 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, |  |  |  | 0 |  | 0 | 0
64 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
65 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C |  |  |  | 0 |  | 0 | 0
66 | Valid |  |  |  |  | Loose-tybe, Gel-Filled Type (SAES-T-928, 5.8) |  |  |  | 0 |  | 0 | 0
67 | Valid |  |  |  |  | - Wrapping : MICA tape (If Fire resistant) |  |  |  | 0 |  | 0 | 0
68 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar (SAES-T-624, 5.2.4.8) |  |  |  | 0 |  | 0 | 0
69 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Black, minimum 2.35% carbon black concentration, Resistant to Ultra violet light,crude oil, hydrocarbons. |  |  |  | 0 |  | 0 | 0
70 | Valid |  |  |  |  | Sulphur compounds and salt water, Low Smoke Zero Halogen (LSZH) |  |  |  | 0 |  | 0 | 0
71 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
72 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
73 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
74 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
75 | Valid |  |  |  |  | - Fire Resistant to BS6387 Cat. C, W, Z |  |  |  | 0 |  | 0 | 0
76 | Valid |  | C.19.1 |  |  |  | 144 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 144 | C | 0 | 0 |  | M367577766B | M | 0
77 | Valid |  | C.19.2 |  |  |  | 96 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 96 | C | 0 | 0 |  | M367577767B | M | 0
78 | Valid |  | C.19.3 |  |  |  | 72 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 72 | C | 0 | 0 |  | M368405062B | M | 0
79 | Valid |  | C.19.4 |  |  |  | 48 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 48 | C | 0 | 0 |  | M367577765B | M | 0
80 | Valid |  | C.19.5 |  |  |  | 24 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 24 | C | 0 | 0 |  | M367577764B | M | 360 | 360 | [33 empty] | FOC SACS
81 | Valid |  | C.19.6 |  |  |  | 12 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 12 | C | 0 | 0 |  | M367577768B | M | 0
82 | Valid |  | C.19.7 |  |  |  | 4 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 4 | C | 0 | 0 |  | M367577763B | M | 0
83 | Valid |  | C.20 |  | FIBER OPTIC, FIRE RESISTANCE, AMOURED, OUTDOOR |  |  |  |  | 0 |  | 0 | 0
84 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
85 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, |  |  |  | 0 |  | 0 | 0
86 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
87 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C |  |  |  | 0 |  | 0 | 0
88 | Valid |  |  |  |  | Loose-tybe, Gel-Filled Type (SAES-T-928, 5.8) |  |  |  | 0 |  | 0 | 0
89 | Valid |  |  |  |  | - Wrapping : MICA tape (If Fire resistant) |  |  |  | 0 |  | 0 | 0
90 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar (SAES-T-624, 5.2.4.8) |  |  |  | 0 |  | 0 | 0
91 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Black, minimum 2.35% carbon black concentration, Resistant to Ultra violet light,crude oil, hydrocarbons. |  |  |  | 0 |  | 0 | 0
92 | Valid |  |  |  |  | Sulphur compounds and salt water, Low Smoke Zero Halogen (LSZH) |  |  |  | 0 |  | 0 | 0
93 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
94 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
95 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
96 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
97 | Valid |  | C.20.1 |  |  |  | 72 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 72 | C | 0 | 0 |  | M268623721A | M | 0
98 | Valid |  | C.20.2 |  |  |  | 24 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 24 | C | 0 | 0 |  | M268623717A | M | 0
99 | Valid |  | C.20.3 |  |  |  | 12 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 12 | C | 0 | 0 |  | M268623718A | M | 0
100 | Valid |  | C.20.4 |  |  |  | 4 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 4 | C | 0 | 0 |  | M268623730A | M | 0
101 | Valid |  | C.21 |  | FIBER OPTIC, FIRE RESISTANCE, AMOURED, INDOOR |  |  |  |  | 0 |  | 0 | 0
102 | Valid |  |  |  |  | <Complied with Cl.4.11 of PP-824554> |  |  |  | 0 |  | 0 | 0
103 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
104 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, 1310nm wavelength |  |  |  | 0 |  | 0 | 0
105 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
106 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C - Housing : Tight Buffer - two(2) layer coating. The first layer shall be a plastic (protective) coating, the second shall be |  |  |  | 0 |  | 0 | 0
107 | Valid |  |  |  |  | acrylate (to repel moisture) |  |  |  | 0 |  | 0 | 0
108 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar |  |  |  | 0 |  | 0 | 0
109 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Resistant to Ultraviolet light, crude oil, hydrocarbons, Sulphur compounds and salt water, |  |  |  | 0 |  | 0 | 0
110 | Valid |  |  |  |  | Yellow Outer jacket/LSZH-Low Smoke Zero Halogen Outer jacket |  |  |  | 0 |  | 0 | 0
111 | Valid |  |  |  |  | Optical Fiber Non-conductive Plenum (OFNP) type with or without non-metallic moisture barrier |  |  |  | 0 |  | 0 | 0
112 | Valid |  |  |  |  | and shall be listed as being suitable for the purpose, listed as being resistant to spread of fire in accordance with the NEC Article 770 Section 770-26, |  |  |  | 0 |  | 0 | 0
113 | Valid |  |  |  |  | installed in accordance with Section 770-110, and marked in accordance with Table 770-179 |  |  |  | 0 |  | 0 | 0
114 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
115 | Valid |  |  |  |  | - Fire rated : NFPA 70 (NEC article 770) |  |  |  | 0 |  | 0 | 0
116 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
117 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
118 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
119 | Valid |  |  |  |  | - All SYSTEM cables shall be "Indoor Fire-resistant cable" type. |  |  |  | 0 |  | 0 | 0
120 | Valid |  | C.21.1 |  |  |  | 24 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 24 | C | 0 | 0 |  | M268623717C | M | 0
121 | Valid |  | C.21.2 |  |  |  | 12 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 12 | C | 0 | 0 |  | M268623718C | M | 0
122 | Valid |  | C.21.3 |  |  |  | 4 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 4 | C | 0 | 0 |  | M268623730C | M | 0
123 | Valid |  | C.22 |  | ETHERNET CABLE |  |  |  |  | 0 |  | 0 | 0
124 | Valid |  |  |  |  | Unsheilded Twisted Pair Cable |  |  |  | 0 |  | 0 | 0
125 | Valid |  |  |  |  | - Separator Material : Flame Retardant Polyolefin |  |  |  | 0 |  | 0 | 0
126 | Valid |  |  |  |  | - Number of Pairs : 4 |  |  |  | 0 |  | 0 | 0
127 | Valid |  |  |  |  | - Cable Pair Color Coding : T568A |  |  |  | 0 |  | 0 | 0
128 | Valid |  |  |  |  | - Conductors : Solid Annealed Copper |  |  |  | 0 |  | 0 | 0
129 | Valid |  |  |  |  | - Conductor Size : 23 AWG |  |  |  | 0 |  | 0 | 0
130 | Valid |  |  |  |  | - Category 6 |  |  |  | 0 |  | 0 | 0
131 | Valid |  |  |  |  | - Reference Specification PP-824554, Section 4.3 |  |  |  | 0 |  | 0 | 0
132 | Valid |  |  |  |  | - UL listed |  |  |  | 0 |  | 0 | 0
133 | Valid |  |  |  |  | - Fire rated : NFPA 70 (NEC article 770) |  |  |  | 0 |  | 0 | 0
134 | Valid |  | C.22.1 |  |  | LS-CMP(Low smoke Plenum) UTP cable | 4 x P x 23AWG | LS-CMP(Low smoke Plenum) UTP, TE | EC04ZZ06AF14AL04ZZ99ZZ99 | 4 | P | 23 | 0 | AWG | M367577797C | M | 14400 | [6 empty] | 1980 | 10800 |  |  | 1620
135 | Valid |  | C.22.2 |  |  | Gel-Filled UTP Cable (Suitable for Direct Burial and OSP) | 4 x P x 23AWG | Gel-Filled UTP, TE | EC04ZZ06AF14AL04ZZ99ZZ99 | 4 | P | 23 | 0 | AWG | M367577797D | M | 0
136 | Valid |  | C.23 |  | Twisted Pair Cable for Telecommunication System |  |  |  |  | 0 |  | 0 | 0
137 | Valid |  |  |  |  | Twisted Pair, Non Shielded, Armoured, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
138 | Valid |  |  |  |  | Without Overall Shield. |  |  |  | 0 |  | 0 | 0
139 | Valid |  |  |  |  | Steel Wired Armoured |  |  |  | 0 |  | 0 | 0
140 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
141 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
142 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
143 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
144 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant / Gas Blocking |  |  |  | 0 |  | 0 | 0
145 | Valid |  | C.23.1 |  |  |  | 1 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 1 | P | 12 | 0 | AWG | M368405073A | M | 0
146 | Valid |  | C.23.1.1 |  |  |  | 1 x P x 12 AWG | TE, NON ARMROED |  | 1 | P | 12 | 0 | AWG |  | M | 0
147 | Valid |  | C.23.2 |  |  |  | 2 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 2 | P | 12 | 0 | AWG | M368405074A | M | 0
148 | Valid |  | C.23.3 |  |  |  | 6 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 6 | P | 12 | 0 | AWG | M368405075A | M | 0
149 | Valid |  | C.23.4 |  |  |  | 8 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 8 | P | 12 | 0 | AWG | M368405089A | M | 0
150 | Valid |  | C.23.5 |  |  |  | 10 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 10 | P | 12 | 0 | AWG | M368405076A | M | 0
151 | Valid |  |  |  |  | Twisted Pair, Shielded, Armoured, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
152 | Valid |  |  |  |  | Overall Shield, Steel Wired Armoured |  |  |  | 0 |  | 0 | 0
153 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
154 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
155 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
156 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
157 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant / Gas Blocking |  |  |  | 0 |  | 0 | 0
158 | Valid |  | C.23.6 |  |  |  | 2 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 2 | P | 16 | 0 | AWG | M368405063A | M | 0
159 | Valid |  | C.23.7 |  |  |  | 4 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 4 | P | 16 | 0 | AWG | M368405064A | M | 0
160 | Valid |  | C.23.8 |  |  |  | 10 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 10 | P | 16 | 0 | AWG | M368405065A | M | 0
161 | Valid |  | C.23.9 |  |  |  | 2 x P x 18 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 2 | P | 18 | 0 | AWG | M368405066A | M | 0
162 | Valid |  | C.23.10 |  |  |  | 4 x P x 18 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 4 | P | 18 | 0 | AWG | M368405067A | M | 0
163 | Valid |  |  |  |  | Twisted Pair, Shielded, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
164 | Valid |  |  |  |  | Overall Shield |  |  |  | 0 |  | 0 | 0
165 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
166 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
167 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
168 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
169 | Valid |  | C.23.11 |  |  |  | 1 x P x 12 AWG | TE | EC04AA03AL99AL01BA01AB99 | 1 | P | 12 | 0 | AWG | M368405077A | M | 0
170 | Valid |  | C.23.12 |  |  |  | 2 x P x 12 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 12 | 0 | AWG | M368405078A | M | 0
171 | Valid |  | C.23.13 |  |  |  | 2 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 16 | 0 | AWG | M368405079A | M | 0
172 | Valid |  | C.23.14 |  |  |  | 4 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 4 | P | 16 | 0 | AWG | M368405080A | M | 0
173 | Valid |  | C.23.15 |  |  |  | 6 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 6 | P | 16 | 0 | AWG | M368405081A | M | 0
174 | Valid |  | C.23.16 |  |  |  | 1 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 1 | P | 18 | 0 | AWG | M368405090A | M | 0
175 | Valid |  | C.23.17 |  |  |  | 2 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 18 | 0 | AWG | M368405082A | M | 0
176 | Valid |  | C.23.18 |  |  |  | 4 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 4 | P | 18 | 0 | AWG | M368405083A | M | 0
177 | Valid |  | C.24 |  | Telephone Cable for Telecommunication System |  |  |  |  | 0 |  | 0 | 0
178 | Valid |  |  |  |  | - Jelly Filled |  |  |  | 0 |  | 0 | 0
179 | Valid |  |  |  |  | - Single Shielded (Corrugated Aluminum Tape) |  |  |  | 0 |  | 0 | 0
180 | Valid |  |  |  |  | - Core Wapping Tape |  |  |  | 0 |  | 0 | 0
181 | Valid |  |  |  |  | - LDPE outer sheath |  |  |  | 0 |  | 0 | 0
182 | Valid |  |  |  |  | - Steel Tape Armored. |  |  |  | 0 |  | 0 | 0
183 | Valid |  |  |  |  | - For Underground Installation |  |  |  | 0 |  | 0 | 0
184 | Valid |  |  |  |  | - Fire rated : N/A |  |  |  | 0 |  | 0 | 0
185 | Valid |  | C.24.1 |  |  |  | 100 x P x 22 AWG | TE | EC04ZZ99ZZ99AH99ZZ99ZZ99 | 100 | P | 22 | 0 | AWG | M367577788A | M | 0
186 | Valid |  | C.25 |  | RS-485 Cable |  |  |  |  | 0 |  | 0 | 0
187 | Valid |  | C.25.1 |  |  |  | 4 x P x 18 AWG |  |  | 4 | P | 18 | 0 | AWG |  | M | 0
188 | Valid |  | C.25.2 |  |  |  | 2 x P x 22 AWG |  |  | 2 | P | 22 | 0 | AWG |  | M | 0
189 | Valid |  | C.25.3 |  |  |  | 2 x P x 22 AWG | TE |  | 2 | P | 22 | 0 | AWG |  | M | 0
Note on U18: HEC: Assumed Location of UPS PDP at field - PCCTV - Industrial Wifi - Flashin Beacon
Note on U22: HEC: ESS JB Power from PIB
Note on Y36: HEC: Power for the SACS Local Controller
Note on Z36: HEC: Power for the SACS Local Controller
Note on AC36: HEC: Power for the SACS Local Controller
Note on Y40: HEC: UPS Powerx 2 for redundancy - SACS Cabine - PCCTV Cabinet - Data Network
Note on Z40: HEC: UPS Power SACS Cabinet & PCCTV Cabinet & IVPS Cabinet & 2 x UPS Power for Data Network & 2 x Emergency Siren System
Note on AC40: HEC: UPS Powerx 2 for redundancy - SACS Cabinet - PCCTV Cabinet - Data Network Cabinet
Note on Y41: HEC: SACS Local Controller Control Cable
Note on Z41: HEC: SACS Local Controller Control Cable
Note on AC41: HEC: SACS Local Controller Control Cable
Note on U52: HEC: Speaker, PCCTV, Flashing Beacon, ESS Siren JB
Note on Y52: HEC: Speaker, SACS CCTV & PCCTV
Note on Z52: HEC: Speaker, SACS CCTV & PCCTV
Note on AC52: HEC: Speaker, SACS CCTV & PCCTV
Note on U53: HEC: Speaker JB, Remote Amplifiers, Call Station & Industrial Wifi
Note on Y53: HEC: Remote Amplifier
Note on Z53: HEC: Remote Amplifier
Note on AC53: HEC: Remote Amplifier
Note on S87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on V87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on W87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on X87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AA87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AB87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AD87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AE87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AH87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AK87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AL87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AM87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AN87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AO87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AP87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AQ87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on AR87: HEC: FOC Security, Building to Building (SS071-SS070-PIB080)
Note on Y141: HEC: SCS Data Outlet x 2
Note on Z141: HEC: SCS Data Outlet x 2
Note on AC141: HEC: SCS Data Outlet x 2 x 90meters max

## Cable Tray
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Cable Tray Width | Cable Tray Height | Thickness | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[16 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | D |  | LADDER CABLE TRAY |  |  |  |  | 0 | 0
2 | Valid |  |  |  | LADDER CABLE TRAY - OUTDOOR | LADDER CABLE TRAY - OUTDOOR |  |  |  | 0 | 0
3 | Valid |  |  |  |  | CABLE TRAY SHALL BE DESIGNED, MANUFACTURED, RATED, TESTED AND MARKED |  |  |  | 0 | 0
4 | Valid |  |  |  |  | IN ACCORDANCE WITH NEMA VE 1 (REFERENCES : SAES-J-902 & SAES-P-104) |  |  |  | 0 | 0
5 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM (MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
6 | Valid |  |  |  |  | - MATERIAL FOR FASTENERS(BOLT, NUT & WASHER & ETC) : 316SS |  |  |  | 0 | 0
7 | Valid |  |  |  |  | - DISTANCE OF CONSECUTIVE RUNGS : 229MM(9") MAXIMUM |  |  |  | 0 | 0
8 | Valid |  |  |  |  | - RUNG LOAD CAPACITY : 90KG MINIMUM |  |  |  | 0 | 0
9 | Valid |  |  |  |  | - ALLOWABLE DEFLECTION : L/100(L=SPAN LENGTH) MAXIMUM |  |  |  | 0 | 0
10 | Valid |  |  |  |  | - VENTILATED TYPE FLANGED COVER : MINIMUM 1.0 MM THICKNESS |  |  |  | 0 | 0
11 | Valid |  |  |  |  | - TRAY THICKNESS : MANUFACTURE STANDARD (MIN. 3.2mm) |  |  |  | 0 | 0
12 | Valid |  |  |  |  | - LOAD / SPAN CLASSS : 20C AS PER NEMA VE1 |  |  |  | 0 | 0
13 | Valid |  |  |  |  | - OUTSIDE FLANGE |  |  |  | 0 | 0
14 | Valid |  |  |  |  | - SPAN : STANDARD SPAN LENGTH 6M |  |  |  | 0 | 0
15 | Valid |  |  |  |  | - FITTINGS RADIUS : 600mm (OUTDOOR) |  |  |  | 0 | 0
16 | Valid |  | D.1 |  | STRAIGHT TRAY | STRAIGHT CABLE TRAY |  |  |  | 0 | 0
17 | Valid |  |  |  |  | - BODY LENGTH : 6.0M |  |  |  | 0 | 0
18 | Valid |  | D.1.1 |  |  | LADDER TRAY STRAIGHT | 152 mm(6") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 150 | 150 | 3.0 | M414586722A | M | 0
19 | Valid |  | D.1.2 |  |  | LADDER TRAY STRAIGHT | 305 mm(12") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 300 | 150 | 3.0 | M414586723A | M | 0
20 | Valid |  | D.1.3 |  |  | LADDER TRAY STRAIGHT | 610 mm(24") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 600 | 150 | 3.0 | M414586724A | M | 0
21 | Valid |  | D.1.4 |  |  | LADDER TRAY STRAIGHT | 915 mm(36") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 900 | 150 | 3.0 | M414586725A | M | 3000 |  |  | 3000 | [31 empty] | CCTV Power & FOC, Security & Paging
22 | Valid |  | D.2 |  | STRAIGHT CABLE TRAY COVER | STRAIGHT CABLE TRAY COVER |  |  |  | 0 | 0
23 | Valid |  |  |  |  | - COVER LENGTH : 3.0M |  |  |  | 0 | 0
24 | Valid |  | D.2.1 |  |  | LADDER TRAY STRAIGHT COVER | 152mm (6") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 150 | 0 | 1 | M349322046A | M | 0
25 | Valid |  | D.2.2 |  |  | LADDER TRAY STRAIGHT COVER | 305 mm(12") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 300 | 0 | 1 | M349322047A | M | 0
26 | Valid |  | D.2.3 |  |  | LADDER TRAY STRAIGHT COVER | 610 mm(24") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 600 | 0 | 1 | M349322048A | M | 0
27 | Valid |  | D.2.4 |  |  | LADDER TRAY STRAIGHT COVER | 915 mm(36") (W)) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 900 | 0 | 1 | M349322049A | M | 3000 |  |  | 3000 | [31 empty] | CCTV Power & FOC, Security & Paging
28 | Valid |  | D.3 |  | HORIZONTAL ELBOW | HORIZONTAL ELBOW (90DEG) WITH COVERS |  |  |  | 0 | 0
29 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
30 | Valid |  | D.3.1 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 150 | 150 | 2.0 | M414586726A | EA | 0
31 | Valid |  | D.3.2 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 300 | 150 | 2.0 | M414586727A | EA | 0
32 | Valid |  | D.3.3 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 600 | 150 | 2.0 | M414586728A | EA | 0
33 | Valid |  | D.3.4 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 900 | 150 | 2.0 | M414586729A | EA | 20 |  |  | 20
34 | Valid |  | D.4 |  | HORIZONTAL TEE | HORIZONTAL TEE WITH COVERS |  |  |  | 0 | 0
35 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
36 | Valid |  | D.4.1 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 150 | 150 | 2.0 | M414586730A | EA | 0
37 | Valid |  | D.4.2 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 300 | 150 | 2.0 | M414586731A | EA | 0
38 | Valid |  | D.4.3 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 600 | 150 | 2.0 | M414586732A | EA | 0
39 | Valid |  | D.4.4 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 900 | 150 | 2.0 | M414586733A | EA | 20 |  |  | 20
40 | Valid |  | D.5 |  | HORIZONTAL CROSS | HORIZONTAL CROSS WITH COVERS |  |  |  | 0 | 0
41 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
42 | Valid |  | D.5.1 |  |  | LADDER TRAY HORIZONTAL CROSS WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AA03ZZ99ZZ | 300 | 150 | 2.0 | M414586734A | EA | 0
43 | Valid |  | D.6 |  | VERTICAL ELBOW INSIDE | VERTICAL ELBOW (90DEG) INSIDE WITH COVERS |  |  |  | 0 | 0
44 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
45 | Valid |  | D.6.1 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 150 | 150 | 2.0 | M414586735A | EA | 0
46 | Valid |  | D.6.2 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 300 | 150 | 2.0 | M414586736A | EA | 0
47 | Valid |  | D.6.3 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 600 | 150 | 2.0 | M414586737A | EA | 0
48 | Valid |  | D.6.4 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 900 | 150 | 2.0 | M414586738A | EA | 20 |  |  | 20
49 | Valid |  | D.7 |  | VERTICAL ELBOW OUTSIDE | VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS |  |  |  | 0 | 0
50 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
51 | Valid |  | D.7.1 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 150 | 150 | 2.0 | M414586739A | EA | 0
52 | Valid |  | D.7.2 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 300 | 150 | 2.0 | M414586740A | EA | 0
53 | Valid |  | D.7.3 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 600 | 150 | 2.0 | M414586741A | EA | 0
54 | Valid |  | D.7.4 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 900 | 150 | 2.0 | M414586742A | EA | 20 |  |  | 20
55 | Valid |  | D.8 |  | REDUCING SPLICE PLATE | REDUCING SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
56 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
57 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
58 | Valid |  | D.8.1 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ99ZZ | 150 | 150 | 2.0 | M414586743A | EA | 0
59 | Valid |  | D.8.2 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 300 mm x 150 mm x 2 mm | OUTDOOR TYPE 1 | ET01AB99ZZ99ZZ99ZZ | 300 | 150 | 2.0 | M414586744A | EA | 0
60 | Valid |  | D.8.3 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 600 mm x 150 mm x 2 mm | OUTDOOR TYPE 2 | ET01AB99ZZ99ZZ99ZZ | 600 | 150 | 2.0 | M414586745A | EA | 0
61 | Valid |  | D.8.4 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 750 mm x 150 mm x 2.6 mm | OUTDOOR TYPE 3 | ET01AB99ZZ99ZZ99ZZ | 750 | 150 | 2.6 | M421387043A | EA | 0
62 | Valid |  | D.9 |  | ADJUSTABLE HORIZONTAL CONNECTOR | ADJUSTABLE HORIZONTAL CONNECTOR |  |  |  | 0 | 0
63 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
64 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
65 | Valid |  | D.9.1 |  |  | LADDER TRAY ADJUSTABLE HORIZONTAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | OUTDOOR TYPE 1 | ET01AB99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M349322058C | EA | 0
66 | Valid |  | D.10 |  | ADJUSTABLE VERTICAL CONNECTOR | ADJUSTABLE VERTICAL CONNECTOR |  |  |  | 0 | 0
67 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
68 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
69 | Valid |  | D.10.1 |  |  | LADDER TRAY ADJUSTABLE VERTICAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | OUTDOOR TYPE 2 | ET01AB99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M349322058D | EA | 0
70 | Valid |  | D.11 |  | BLIND END PLATE | BLIND END PLATE |  |  |  | 0 | 0
71 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
72 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
73 | Valid |  | D.11.1 |  |  | LADDER TRAY BLIND END PLATE | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 150 | 150 | 2.0 | M393921564B | EA | 0
74 | Valid |  | D.11.2 |  |  | LADDER TRAY BLIND END PLATE | 300 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 300 | 150 | 2.0 | M393921565C | EA | 0
75 | Valid |  | D.11.3 |  |  | LADDER TRAY BLIND END PLATE | 600 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 600 | 150 | 2.0 | M393921566B | EA | 0
76 | Valid |  | D.11.4 |  |  | LADDER TRAY BLIND END PLATE | 900 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 900 | 150 | 2.0 | M393921567B | EA | 20 |  |  | 20
77 | Valid |  | D.12 |  | SPLICE PLATE | HEAVY DUTY SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
78 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
79 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
80 | Valid |  | D.12.1 |  |  | LADDER TRAY SPLICE PLATE | 140 mm x 3 mm | OUTDOOR | ET01AB99ZZ99ZZ14ZZ | 0 | 140 | 3.0 | M365749320A | EA | 0
81 | Valid |  | D.13 |  | HEAVY DUTY EXPANSION SPLICE PLATE | HEAVY DUTY EXPANSION SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
82 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
83 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
84 | Valid |  | D.13.1 |  |  | LADDER TRAY HEAVY DUTY EXPANSION SPLICE PLATE | 140 mm x 3 mm | OUTDOOR | ET01AB99ZZ99ZZ08ZZ | 0 | 140 | 3.0 | M414586751A | EA | 0
85 | Valid |  | D.14 |  | GROUND BONDING JUMPER | GROUND BONDING JUMPER |  |  |  | 0 | 0
86 | Valid |  |  |  |  | - MATERIAL : INSULATED COPPER WIRED GROUND CABLE (GREEN &YELLOW TRACER) |  |  |  | 0 | 0
87 | Valid |  |  |  |  | - 35 SQMM x 400 MM LENGTH W/TERMINAL LUG (TINNED COPPER) |  |  |  | 0 | 0
88 | Valid |  |  |  |  | - ACCESSORIES : 316SS SHANK BOLTS & NUTS, WASHER |  |  |  | 0 | 0
89 | Valid |  | D.14.1 |  |  | LADDER TRAY GROUND BONDING JUMPER | None | OUTDOOR | ET01AD99ZZ99ZZ01ZZ | 0 | 0 | 0 | M214244783F | EA | 1000 |  |  | 1000 | [31 empty] | CCTV Power & FOC, Security & Paging
90 | Valid |  | D.15 |  | HOLD DOWN CLAMP | HOLD DOWN CLAMP |  |  |  | 0 | 0
91 | Valid |  |  |  |  | - MATERIAL : STAINLESS STEEL(316SS) |  |  |  | 0 | 0
92 | Valid |  |  |  |  | - ACCESSORIES : 316SS BOLT & NUT, WASHER |  |  |  | 0 | 0
93 | Valid |  | D.15.1 |  |  | BEAM CLAMP TYPE FOR HORIZONTAL LADDER CABLE TRAY | None | OUTDOOR | ET01AI99ZZ99ZZ19ZZ | 0 | 0 | 0 | M286458936B | EA | 0 | [34 empty] | CCTV Power & FOC, Security & Paging
94 | Valid |  | D.15.2 |  |  | BEAM GUIDE TYPE FOR HORIZONTAL LADDER CABLE TRAY | None | OUTDOOR TYPE 1 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167M | EA | 0
95 | Valid |  | D.15.3 |  |  | HOLD DOWN BRACKET 2 HOLE (FOR VERTICAL PARTS) | None | OUTDOOR | ET01AI99ZZ99ZZ13ZZ | 0 | 0 | 0 | M349322296B | EA | 0
96 | Valid |  | D.15.4 |  |  | HOLD DOWN CLAMP WITH SPRING NUT (For U-Channel) | None | OUTDOOR TYPE 2 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167N | EA | 0
97 | Valid |  | D.15.5 |  |  | GUIDE TYPE CLAMP WITH SPRING NUT (For U-Channel) | None | OUTDOOR TYPE 3 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167O | EA | 0
98 | Valid |  | D.15.6 |  |  | HOLD DOWN BRACKET 4 HOLE (FOR VERTICAL PARTS) | None | OUTDOOR | ET01AI99ZZ99ZZ99ZZ | 0 | 0 | 0 | M272892167B | EA | 0
99 | Valid |  | D.16 |  | HEAVY DUTY CABLE TRAY COVER CLAMP | HEAVY DUTY CABLE TRAY COVER CLAMP |  |  |  | 0 | 0
100 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
101 | Valid |  |  |  |  | - COMPLETE WITH BOLT & NUTS & WWASHER : 316SS |  |  |  | 0 | 0
102 | Valid |  |  |  |  | - COMPLETE WITH NON-METALIC WASHER(GASKET) SUCH AS TEFLON OR NITRILE RUBBER TO WITHSTAND CORROSION |  |  |  | 0 | 0
103 | Valid |  | D.16.1 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 150 | 150 | 2.0 | M414586746A | EA | 0
104 | Valid |  | D.16.2 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 300 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 300 | 150 | 2.0 | M414586747A | EA | 0
105 | Valid |  | D.16.3 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 600 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 600 | 150 | 2.0 | M414586748A | EA | 0
106 | Valid |  | D.16.4 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 900 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 900 | 150 | 2.0 | M414586749A | EA | 3000 |  |  | 3000
107 | Valid |  |  |  | LADDER CABLE TRAY - INDOOR | LADDER CABLE TRAY - INDOOR |  |  |  | 0 | 0
108 | Valid |  |  |  |  | CABLE TRAY SHALL BE DESIGNED, MANUFACTURED, RATED, TESTED AND MARKED |  |  |  | 0 | 0
109 | Valid |  |  |  |  | IN ACCORDANCE WITH NEMA VE 1 (REFERENCES : SAES-J-902 & SAES-P-104) |  |  |  | 0 | 0
110 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM (MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
111 | Valid |  |  |  |  | - MATERIAL FOR FASTENERS(BOLT, NUT & WASHER & ETC) : 316SS |  |  |  | 0 | 0
112 | Valid |  |  |  |  | - DISTANCE OF CONSECUTIVE RUNGS : 229MM(9") MAXIMUM |  |  |  | 0 | 0
113 | Valid |  |  |  |  | - RUNG LOAD CAPACITY : 90KG MINIMUM |  |  |  | 0 | 0
114 | Valid |  |  |  |  | - ALLOWABLE DEFLECTION : L/100(L=SPAN LENGTH) MAXIMUM |  |  |  | 0 | 0
115 | Valid |  |  |  |  | - TRAY THICKNESS : MANUFACTURE STANDARD (MIN. 3.2mm) |  |  |  | 0 | 0
116 | Valid |  |  |  |  | - LOAD / SPAN CLASSS : 20C AS PER NEMA VE1 |  |  |  | 0 | 0
117 | Valid |  |  |  |  | - OUTSIDE FLANGE |  |  |  | 0 | 0
118 | Valid |  |  |  |  | - SPAN : STANDARD SPAN LENGTH 6M |  |  |  | 0 | 0
119 | Valid |  |  |  |  | - FITTINGS RADIUS : 300mm (INDOOR) |  |  |  | 0 | 0
120 | Valid |  | D.17 |  | STRAIGHT TRAY | STRAIGHT CABLE TRAY |  |  |  | 0 | 0
121 | Valid |  |  |  |  | - BODY LENGTH : 6.0M |  |  |  | 0 | 0
122 | Valid |  | D.17.1 |  |  | LADDER TRAY STRAIGHT | 152 mm(6") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 150 | 150 | 3.0 | M414586722B | M | 840 | [6 empty] | 240 | 360 |  |  | 240 | [23 empty] | SACS UPS Power & Controller
123 | Valid |  | D.17.2 |  |  | LADDER TRAY STRAIGHT | 305 mm(12") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 300 | 150 | 3.0 | M414586723B | M | 600 | [6 empty] | 200 | 200 |  |  | 200
124 | Valid |  | D.17.3 |  |  | LADDER TRAY STRAIGHT | 457 mm(18") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 450 | 150 | 3.0 | M414586750A | M | 0
125 | Valid |  | D.17.4 |  |  | LADDER TRAY STRAIGHT | 610 mm(24") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 600 | 150 | 3.0 | M414586724B | M | 0
126 | Valid |  | D.17.5 |  |  | LADDER TRAY STRAIGHT | 915 mm(36") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 900 | 150 | 3.0 | M414586725B | M | 0
127 | Valid |  | D.18 |  | HORIZONTAL ELBOW | HORIZONTAL ELBOW (90DEG) WITHOUT COVERS |  |  |  | 0 | 0
128 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
129 | Valid |  | D.18.1 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 150 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 150 | 150 | 2.0 | M414586726B | EA | 15 | [6 empty] | 5 | 5 |  |  | 5
130 | Valid |  | D.18.2 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 300 | 150 | 2.0 | M414586727B | EA | 15 | [6 empty] | 5 | 5 |  |  | 5
131 | Valid |  | D.18.3 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 600 | 150 | 2.0 | M414586728B | EA | 0
132 | Valid |  | D.18.4 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 900 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 900 | 150 | 2.0 | M414586729B | EA | 0
133 | Valid |  | D.18.5 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 450 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 450 | 150 | 2 | M421387044A | EA | 0
134 | Valid |  |  |  |  | - RADIUS : 300mm |  |  |  | 0 | 0
135 | Valid |  | D.18.6 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ02ZZ | 300 | 150 | 2 | M421387045A | EA | 15 | [6 empty] | 5 | 5 |  |  | 5
136 | Valid |  | D.18.7 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ02ZZ | 600 | 150 | 2 | M421387046A | EA | 0
137 | Valid |  | D.19 |  | HORIZONTAL TEE | HORIZONTAL TEE WITHOUT COVERS |  |  |  | 0 | 0
138 | Valid |  |  |  |  | - RADIUS : 300mm |  |  |  | 0 | 0
139 | Valid |  | D.19.1 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 300 | 150 | 2.0 | M414586731B | EA | 15 | [6 empty] | 5 | 5 |  |  | 5
140 | Valid |  | D.19.2 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 600 | 150 | 2.0 | M414586732B | EA | 0
141 | Valid |  | D.19.3 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 900 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 900 | 150 | 2.0 | M414586733B | EA | 0
142 | Valid |  | D.20 |  | REDUCING SPLICE PLATE | REDUCING SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
143 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
144 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
145 | Valid |  | D.20.1 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 600 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 600 | 150 | 2.0 | M414586745B | EA | 0
146 | Valid |  | D.20.2 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 300 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 300 | 150 | 2 | M414586744B | EA | 0
147 | Valid |  | D.20.3 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 450 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 450 | 150 | 2 | M421387047A | EA | 0
148 | Valid |  | D.21 |  | ADJUSTABLE HORIZONTAL CONNECTOR | ADJUSTABLE HORIZONTAL CONNECTOR |  |  |  | 0 | 0
149 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
150 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
151 | Valid |  | D.21.1 |  |  | ADJUSTABLE HORIZONTAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | INDOOR | ET01AI99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M367485430A | EA | 0
152 | Valid |  | D.22 |  | ADJUSTABLE VERTICAL CONNECTOR | ADJUSTABLE VERTICAL RISER CONNECTOR |  |  |  | 0 | 0
153 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
154 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
155 | Valid |  | D.22.1 |  |  | ADJUSTABLE VERTICAL RISER CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | INDOOR | ET01AI99ZZ99ZZ12ZZ | 0 | 150 | 3.0 | M367485431A | EA | 0
156 | Valid |  | D.23 |  | BLIND END PLATE | BLIND END PLATE |  |  |  | 0 | 0
157 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
158 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
159 | Valid |  | D.23.1 |  |  | LADDER TRAY BLIND END PLATE | 300 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 300 | 150 | 2.0 | M393921565D | EA | 15 | [6 empty] | 5 | 5 |  |  | 5
160 | Valid |  | D.23.2 |  |  | LADDER TRAY BLIND END PLATE | 600 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 600 | 150 | 2.0 | M393921566C | EA | 0
161 | Valid |  | D.23.3 |  |  | LADDER TRAY BLIND END PLATE | 900 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 900 | 150 | 2.0 | M393921567C | EA | 0
162 | Valid |  | D.24 |  | SPLICE PLATE | SPLICE PLATE |  |  |  | 0 | 0
163 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
164 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
165 | Valid |  | D.24.1 |  |  | SPLICE PLATE | 140 mm x 3 mm | INDOOR | ET01AB99ZZ99ZZ14ZZ | 0 | 140 | 3.0 | M365749320B | EA | 0
166 | Valid |  | D.25 |  | GROUND BONDING JUMPER | GROUND BONDING JUMPER |  |  |  | 0 | 0
167 | Valid |  |  |  |  | - MATERIAL : INSULATED COPPER WIRED GROUND CABLE (GREEN &YELLOW TRACER) |  |  |  | 0 | 0
168 | Valid |  |  |  |  | - 35 SQMM x 400 MM LENGTH W/TERMINAL LUG |  |  |  | 0 | 0
169 | Valid |  |  |  |  | - ACCESSORIES : 316SS SHANK BOLTS & NUTS, WASHER |  |  |  | 0 | 0
170 | Valid |  | D.25.1 |  |  | GROUND BONDING JUMPER | None | INDOOR | ET01AD99ZZ99ZZ01ZZ | 0 | 0 | 0 | M214244783G | EA | 0 | [6 empty] | 0 | 0 |  |  | 0 | [23 empty] | SACS UPS Power & Controller
171 | Valid |  | D.26 |  | HOLD DOWN CLAMP | HOLD DOWN CLAMP |  |  |  | 0 | 0
172 | Valid |  |  |  |  | - MATERIAL : 316SS |  |  |  | 0 | 0
173 | Valid |  |  |  |  | - ACCESSORIES : 316SS BOLT & NUT, WASHER |  |  |  | 0 | 0
174 | Valid |  | D.26.1 |  |  | HOLD DOWN CLAMP | None | INDOOR | ET01AI99ZZ99ZZ10ZZ | 0 | 0 |  | M286458938N | EA | 0 | [6 empty] | 0 | 0 |  |  | 0 | [23 empty] | SACS UPS Power & Controller
175 | Valid |  |  |  |  | 177667 |  |  |  | 0 | 0
176 | Valid |  |  |  |  | 149709 |  |  |  | 0 | 0
Note on S26: HEC: - PCCTV - WLAN - IVPS
Note on S32: HEC: - PCCTV - WLAN - IVPS

## Conduit
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Conduit Size | Unit of Conduit Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [7 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[15 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | G |  | CONDUIT
2 | Valid |  | G.1 |  | RIGID STEEL GALVANIZED CONDUIT (RSGC)
3 | Valid |  |  |  |  | - ANSI C80.1 RIGID GALVANIZED STEEL WITH PVC COATED
4 | Valid |  |  |  |  | (MIN. TKS OF PVC : 40 MILS (1MM) PER NEMA RN1.)
5 | Valid |  |  |  |  | - BOTH ENDS NPT THREADED WITH COUPLING SCREWED ON ONE ENDS.
6 | Valid |  | G.1.1 |  |  | LENGTH : 3M | 1" | For Instrument | EU04AI02AC07 | 1 | inch | M220652764C | M | 0
7 | Valid |  | G.1.2 |  |  | LENGTH : 3M | 1-1/4" | For Instrument | EU04AI02AC07 | 1.25 | inch | M220652765A | M | 0
8 | Valid |  | G.1.3 |  |  | LENGTH : 3M | 1-1/2" | For Instrument | EU04AI02AC07 | 1.5 | inch | M220652766B | M | 0
9 | Valid |  | G.1.4 |  |  | LENGTH : 3M | 2" | For Instrument | EU04AI02AC07 | 2 | inch | M220652767B | M | 0
10 | Valid |  | G.1.5 |  |  | LENGTH : 3M | 4" | For Instrument | EU04AI02AC07 | 4 | inch | M347616303A | M | 0
11 | Valid |  | G.1.6 |  |  | LENGTH : 3M | 3/4" | For Telecom | EU04AI02AC07 | 0.75 | inch | M220652763A | M | 0
12 | Valid |  | G.1.7 |  |  | LENGTH : 3M | 1" | For Telecom | EU04AI02AC07 | 1 | inch | M220652764B | M | 300 |  |  | 300 | [31 empty] | for branching out from main tray
13 | Valid |  | G.1.8 |  |  | LENGTH : 3M | 1-1/2" | For Telecom | EU04AI02AC07 | 1.5 | inch | M220652766A | M | 0
14 | Valid |  | G.1.9 |  |  | LENGTH : 3M | 2-1/2" | For Telecom | EU04AI02AC07 | 2.5 | inch | M414586752A | M | 0
15 | Valid |  | G.1.10 |  |  | LENGTH : 3M | 1-1/4" | For Telecom | EU04AI02AC07 | 1.25 | inch | M220652765B | M | 0
16 | Valid |  | G.1.12 |  |  | LENGTH : 3M | 4" | For Telecom | EU04AI02AC07 | 4 | inch | M347616303B | M | 0
17 | Valid |  | G.2 |  | PVC PIPE CONDUIT
18 | Valid |  |  |  |  | - DB-120 As per NEMA TC 6 & 8
19 | Valid |  |  |  |  | - Colored Gray, With One Coupling
20 | Valid |  | G.2.1 |  |  | LENGTH : 6M | 1" | For Telecom | EU03AB99ZZ99 | 1 | inch | M191110753D | M | 3000 |  |  | 3000 | [31 empty] | outdoor lateral runs connecting outdoor cameras, paging intercoms , and outdoor WAP enclosures to nearest routing points
21 | Valid |  | G.2.2 |  |  | LENGTH : 6M | 1-1/4" | For Telecom | EU03AB99ZZ99 | 1.25 | inch | M220652663B | M | 0
22 | Valid |  | G.2.3 |  |  | LENGTH : 6M | 2" | For Telecom | EU03AB99ZZ99 | 2 | inch | M190965498H | M | 0
23 | Valid |  | G.2.4 |  |  | LENGTH : 6M | 4" | For Telecom | EU03AB99ZZ99 | 4 | inch | M190965501F | M | 0
24 | Valid |  | G.2.5 |  |  | LENGTH : 6M | 6" | For Instrument | EU03AB99ZZ99 | 6 | inch | M347616320D | M | 0
25 | Valid |  | G.2.5.1 |  |  | LENGTH : 6M | 1-1/2" | For Telecom | EU03AB99ZZ99 | 1.5 | inch | M190965497A | M | 0
26 | Valid |  | G.2.5.2 |  |  | LENGTH : 6M | 4" | For Instrument | EU03AB99ZZ99 | 4 | inch | M190965501I | M | 0
27 | Valid |  |  |  |  | - TYPE EB-20, NEMA TC 6 & 8
28 | Valid |  |  |  |  | - Colored Gray, Without Coupling
29 | Valid |  | G.2.6 |  |  | LENGTH : 3M | 2" | FOR WALL OPENING | EU03AB99ZZ99 | 2 | inch | M190965498G | M | 0
30 | Valid |  | G.2.7 |  |  | LENGTH : 3M | 3" | FOR WALL OPENING | EU03AB99ZZ99 | 3 | inch | M190965500D | M | 0
31 | Valid |  | G.2.8 |  |  | LENGTH : 3M | 1" | FOR WALL OPENING | EU03AB99ZZ99 | 1 | inch | M191110753E | M | 0
32 | Valid |  | G.3 |  | EMT CONDUIT
33 | Valid |  |  |  |  | - ANSI C80.3, UL797
34 | Valid |  |  |  |  | - WITH ONE END COUPLING
35 | Valid |  | G.3.1 |  |  | LENGTH : 6M | 1" | For Telecom | EU04AM05AB99 | 1 | inch | M367575811B | M | 940 | [6 empty] | 120 | 700 |  |  | 120
36 | Valid |  | G.3.2 |  |  | LENGTH : 6M | 1-1/4" | For Telecom | EU04AM05AB99 | 1.25 | inch | M367575812B | M | 0
37 | Valid |  | G.3.3 |  |  | LENGTH : 6M | 1-1/2" | For Telecom | EU04AM05AB99 | 1.5 | inch | M368407344A | M | 0
38 | Valid |  | G.3.4 |  |  | LENGTH : 6M | 2" | For Telecom | EU04AM05AB99 | 2 | inch | M368407345A | M | 40 | [6 empty] | 20 |  |  |  | 20
39 | Valid |  | G.3.5 |  |  | LENGTH : 6M | 2-1/2" | For Telecom | EU04AM05AB99 | 2.5 | inch | M390258549A | M | 0
40 | Valid |  | G.3.6 |  |  | LENGTH : 6M | 1/2" | For Telecom | EU04AM05AB99 | 0.5 | inch | M414586753A | M | 0
41 | Valid |  | G.3.7 |  |  | LENGTH : 6M | 3/4" | For Telecom | EU04AM05AB99 | 0.75 | inch | M414586754A | M | 0
42 | Valid |  | G.4 |  | Corrugated Optical Duct (C.O.D)
43 | Valid |  |  |  |  | - HDPE corrugated pipe with 110mm (4") outer diameter, orange color
44 | Valid |  | G.4.1 |  |  | C.O.D with 5-1" Sub-ducts with pulling rope, 5 sub-duct color code : Blue/Orange/Green/White/Black | 4" | C.O.D with 5-1" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826A | M | 12364.8 |  |  | 12364.8 | [31 empty] | FO CCTV
45 | Valid |  | G.4.2 |  |  | C.O.D with 4-1 1/4" Sub-ducts with pulling rope, 4 sub-duct color code : Blue/Orange/Green/White | 4" | C.O.D with 4-1 1/4" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826B | M | 0
46 | Valid |  | G.4.3 |  |  | C.O.D with 3-1 1/2" Sub-ducts with pulling rope, 3 sub-duct color code : Orange/Green/White | 4" | C.O.D with 3-1 1/2" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826C | M | 0
47 | Valid |  | G.4.4 |  |  | C.O.D without Sub-duct | 4" | C.O.D without Sub-duct | EU02AG05AB99 | 4 | inch | M367575826D | M | 0
48 | Valid |  | G.4.5 |  |  | C.O.D without Sub-duct | 150 mm | C.O.D without Sub-duct | EU02AG05AB99 | 150 | mm | M414586757A | M | 0
49 | Valid |  | G.5 |  | Flexible Conduit
50 | Valid |  |  |  |  | - UL LIQUIDTIGHT FLEXIBLE METAL CONDUIT (FOR CLASS 1, ZONE 2) WITH PVC COATED
51 | Valid |  |  |  |  | - TEMPERATURE RATING ≥ 80℃
52 | Valid |  | G.5.1 |  |  |  | 1" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 1 | inch | M368429397D | M | 0
53 | Valid |  | G.5.2 |  |  |  | 1-1/2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 1.5 | inch | M368429398D | M | 0
54 | Valid |  | G.5.3 |  |  |  | 2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 2 | inch | M368429399B | M | 0
55 | Valid |  | G.5.4 |  |  |  | 2-1/2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 2.5 | inch | M368429400C | M | 0
56 | Valid |  | G.5.5 |  |  |  | 1" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1 | inch | M368429397B | M | 0
57 | Valid |  | G.5.6 |  |  |  | 3/4" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | .75 | inch | M390284338A | EA | 0
58 | Valid |  | G.5.7 |  |  |  | 1/2" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 0.5 | inch | M421387002A | M | 0
59 | Valid |  | G.5.8 |  |  |  | 1-1/4" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1.25 | inch | M421387003A | M | 0
60 | Valid |  | G.5.9 |  |  |  | 1-1/2" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1.5 | inch | M368429398E | M | 0
61 | Valid |  | G.6 |  | FLEXIBLE METALLIC CONDUIT
62 | Valid |  |  |  |  | UL listed, Gavanized Steel Type FMC
63 | Valid |  | G.6.1 |  |  |  | 3/4" | 3/4'', for Telecom | EU02AE02ZZ07 | 0.75 | inch | M390284338B | M | 0
64 | Valid |  | G.6.2 |  |  |  | 1" | 1", for Telecom | EU02AE02ZZ07 | 1 | inch | M368429397C | M | 0
65 | Valid |  | G.6.3 |  |  |  | 1-1/2" | 1-1/2", for Telecom | EU02AE02ZZ07 | 1.5 | inch | M368429398B | M | 0
66 | Valid |  | G.7 |  | HDPE Sub-duct
67 | Valid |  |  |  |  | UL listed, Gavanized Steel Type FMC
68 | Valid |  | G.7.1 |  | HDPE Sub-duct |  | 1" | Green, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016A | M | 180 |  |  | 180
69 | Valid |  | G.7.2 |  | HDPE Sub-duct |  | 1" | Blue, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016B | M | 180 |  |  | 180
70 | Valid |  | G.7.3 |  | HDPE Sub-duct |  | 1" | White, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016C | M | 180 |  |  | 180
71 | Valid |  | G.7.4 |  | HDPE Sub-duct |  | 1" | Orange, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016D | M | 180 |  |  | 180
Note on W40: HEC: SCS
Note on R49: HEC: FO CCTV

## Cable Gland
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Gland Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [6 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[14 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | I |  | CABLE GLAND
2 | Valid |  | I.1 |  | ARMORED CABLE GLAND
3 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
4 | Valid |  |  |  |  | - Seal ring and compound barrier seal
5 | Valid |  |  |  |  | - Sealing ring kit, PCV shroud, Locknut, Earth Tag, Washer
6 | Valid |  |  |  |  | - Material including metal fastener : 316SS
7 | Valid |  |  |  |  | - Shall be designed to bond the armor ( listed as suitable for grounding )
8 | Valid |  |  |  |  | and bond the armored to the gland
9 | Valid |  | I.1.1 |  |  |  | M20 | M20.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318D | EA | 0
10 | Valid |  | I.1.2 |  |  |  | M25 | M25.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 25 | M388017319C | EA | 0
11 | Valid |  | I.1.3 |  |  |  | M32 | M32.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 32 | M388017320C | EA | 0
12 | Valid |  | I.1.4 |  |  |  | M40 | M40.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 40 | M388017321C | EA | 0
13 | Valid |  | I.1.5 |  |  |  | M20 | M20.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318C | EA | 0
14 | Valid |  | I.1.6 |  |  |  | M25 | M25.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 25 | M388017319B | EA | 0
15 | Valid |  | I.1.7 |  |  |  | M32 | M32.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 32 | M388017320B | EA | 0
16 | Valid |  | I.1.8 |  |  |  | M40 | M40.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 40 | M388017321B | EA | 0
17 | Valid |  | I.1.9 |  |  |  | M50 | M50.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 50 | M421387008A | EA | 0
18 | Valid |  | I.1.10 |  |  |  | M20 | M20.M, SEALING RANGE : 2 | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318E | EA | 0
19 | Valid |  | I.2 |  | NON-ARMORED CABLE GLAND
20 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
21 | Valid |  |  |  |  | - Seal ring and compound barrier seal
22 | Valid |  |  |  |  | - Sealing ring kit, PCV shroud, Locknut, Earth Tag, Washer
23 | Valid |  |  |  |  | - Material including metal fastener : 316SS
24 | Valid |  |  |  |  | - METRIC.M X METRIC.F for Flexible Conduit Connection
25 | Valid |  | I.2.1 |  |  |  | M20 | M20.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322E | EA | 0
26 | Valid |  | I.2.2 |  |  |  | M25 | M25.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323F | EA | 0
27 | Valid |  | I.2.3 |  |  |  | M32 | M32.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324G | EA | 0
28 | Valid |  | I.2.4 |  |  |  | M40 | M40.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325G | EA | 0
29 | Valid |  | I.2.5 |  |  |  | M50 | M50.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326F | EA | 0
30 | Valid |  | I.2.6 |  |  |  | M63 | M63.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333D | EA | 0
31 | Valid |  | I.2.7 |  |  |  | M40 | M40.M X M40.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325H | EA | 0
32 | Valid |  | I.2.8 |  |  |  | M50 | M50.M X M50.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326G | EA | 0
33 | Valid |  | I.2.9 |  |  |  | M63 | M63.M X M63.F, SEALING RANGE : 2, | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333E | EA | 0
34 | Valid |  | I.2.10 |  |  |  | 1/2" | 1/2"NPT.M X M20.F, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | .5 | M421387011A | EA | 0
35 | Valid |  | I.2.11 |  |  |  | 3/4" | 3/4"NPT.M X M25.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 0.75 | M421387013A | EA | 0
36 | Valid |  | I.2.12 |  |  |  | M20 | M20.M, NON-ARMORED, FOR TELECOM | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322F | EA | 0
37 | Valid |  | I.2.13 |  |  |  | M25 | M25.M, NON-ARMORED, FOR TELECOM | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323G | EA | 0
38 | Valid |  | I.3 |  | ADAPTOR
39 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
40 | Valid |  |  |  |  | - 316SS, METRIC threaded, 'O' Ring (Male x Female)
41 | Valid |  | I.3.1 |  |  |  | M25 | M20. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323B | EA | 0
42 | Valid |  | I.3.2 |  |  |  | M32 | M20. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324B | EA | 0
43 | Valid |  | I.3.3 |  |  |  | M32 | M25. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324C | EA | 0
44 | Valid |  | I.3.4 |  |  |  | M40 | M25. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325B | EA | 0
45 | Valid |  | I.3.5 |  |  |  | M40 | M32. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325C | EA | 0
46 | Valid |  | I.3.6 |  |  |  | M50 | M32. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326B | EA | 0
47 | Valid |  | I.3.7 |  |  |  | M50 | M40. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326C | EA | 0
48 | Valid |  | I.3.8 |  |  |  | M63 | M40. M x M63. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333A | EA | 0
49 | Valid |  | I.3.9 |  |  |  | M63 | M50. M x M63. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333B | EA | 0
50 | Valid |  | I.3.9.1 |  |  |  | 1/2" | 1/2"NPT(M) x M20(F) | ED03AI99AE01ZZ10AD99ZZ | .5 | M421387011B | EA | 0
51 | Valid |  | I.3.9.2 |  |  |  | 3/4" | 3/4"NPT(M) x M25(F) | ED03AI99AE01ZZ10AD99ZZ | .75 | M421387013B | EA | 0
52 | Valid |  | I.3.9.3 |  |  |  | 1" | 1"NPT(M) x M32(F) | ED03AI99AE01ZZ10AD99ZZ | 1 | M421387009A | EA | 0
53 | Valid |  | I.3.9.4 |  |  |  | 1-1/2" | 1-1/2"NPT(M) x M50(F) | ED03AI99AE01ZZ10AD99ZZ | 1.5 | M421387014A | EA | 0
54 | Valid |  | I.3.9.5 |  |  |  | M20 | M20. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322G | EA | 0
55 | Valid |  | I.3.9.6 |  |  |  | M63 | M63. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333F | EA | 0
56 | Valid |  | I.4 |  | REDUCER
57 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
58 | Valid |  |  |  |  | - 316SS, METRIC threaded, 'O' Ring (Male x Female)
59 | Valid |  | I.4.1 |  |  |  | M20 | M25. M x M20. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322B | EA | 0
60 | Valid |  | I.4.2 |  |  |  | M20 | M32. M x M20. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322C | EA | 0
61 | Valid |  | I.4.3 |  |  |  | M25 | M32. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323C | EA | 0
62 | Valid |  | I.4.4 |  |  |  | M25 | M40. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323D | EA | 0
63 | Valid |  | I.4.5 |  |  |  | M32 | M40. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324D | EA | 0
64 | Valid |  | I.4.6 |  |  |  | M32 | M50. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324E | EA | 0
65 | Valid |  | I.4.7 |  |  |  | M40 | M50. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325D | EA | 0
66 | Valid |  | I.4.8 |  |  |  | M40 | M63. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325E | EA | 0
67 | Valid |  | I.4.9 |  |  |  | M50 | M63. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326D | EA | 0
68 | Valid |  | I.5 |  | PLUG
69 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
70 | Valid |  |  |  |  | - 316SS, METRIC threaded
71 | Valid |  | I.5.1 |  |  |  | M20 | M20.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322D | EA | 0
72 | Valid |  | I.5.2 |  |  |  | M25 | M25.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323E | EA | 0
73 | Valid |  | I.5.3 |  |  |  | M32 | M32.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324F | EA | 0
74 | Valid |  | I.5.4 |  |  |  | M40 | M40.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325F | EA | 0
75 | Valid |  | I.5.5 |  |  |  | M50 | M50.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326E | EA | 0

## Support
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Support Width | Support Height | Support Thickness | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[16 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | Q |  | SUPPORT
2 | Valid |  | Q.1 |  | "U" CHANNEL (UNISTRUT CHANNEL)
3 | Valid |  | Q.1.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 41 x 41 x 2.5t | with APCS-26 Coating, For Instrument | IM23AA | 41 | 41 | 2.5 | M220652813G | M | 0
4 | Valid |  | Q.1.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 41 x 41 x 2.5t |  | IM23AA | 41 | 41 | 2.5 | M220652813 | M | 0
5 | Valid |  | Q.1.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL (Double Type) | 41 x 41 x 2.5t | (Double Type, For Instrument | IM23AA | 41 | 41 | 2.5 | M220652813H | M | 0
6 | Valid |  | Q.1.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 41 x 41 x 2.5t | with APCS-26 Coating, For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813E | M | 0
7 | Valid |  | Q.1.5 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 41 x 41 x 2.5t | For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813F | M | 0
8 | Valid |  | Q.1.6 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL (Double Type) | 82 x 82 x 2.5t | For Telecom | IM23AA | 84 | 41 | 2.6 | M421387020A | M | 0
9 | Valid |  | Q.1.7 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with PVC Coating | 41 x 41 x 2.5t | with PVC Coating, For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813I | EA | 2000 |  |  | 2000
10 | Valid |  | Q.2 |  | "C" CHANNEL
11 | Valid |  | Q.2.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 100 x 50 x 5t | APCS-26 Coating, For Instrument | IM22ZZ | 100 | 50 | 5 | M206428743L | M | 0
12 | Valid |  | Q.2.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 100 x 50 x 5t | For Instrument | IM22ZZ | 100 | 50 | 5 | M206428743M | M | 0
13 | Valid |  | Q.2.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 150 x 75 x 6.5t | APCS-26 Coating, For Instrument | IM22ZZ | 150 | 75 | 6.5 | M222716891C | M | 0
14 | Valid |  | Q.2.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 100 x 50 x 5t | APCS-26 Coating, For Telecom | IM22ZZ | 100 | 50 | 5 | M206428743G | M | 1000 |  |  | 1000
15 | Valid |  | Q.2.5 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 75 x 75 x 5t | APCS-26 Coating , For Telecom | IM22ZZ | 75 | 75 | 5 | M206428767A | M | 0
16 | Valid |  | Q.2.6 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 125 x 65 x 5t | APCS-26 Coating, For Instrument | IM22ZZ | 125 | 65 | 5 | M414586711C | M | 0
17 | Valid |  | Q.3 |  | ANGLE
18 | Valid |  | Q.3.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 50 x 50 x 6t | APCS-26 Coating, For Instrument | IM21ZZ | 50 | 50 | 6 | M209850335I | M | 0
19 | Valid |  | Q.3.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 50 x 50 x 6t | For Instrument | IM21ZZ | 50 | 50 | 6 | M209850335J | M | 0
20 | Valid |  | Q.3.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 50 x 50 x 6t | APCS-26 Coating, For Telecom | IM21ZZ | 50 | 50 | 6 | M209850335E | M | 1000 |  |  | 1000
21 | Valid |  | Q.3.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 75 x 75 x 6t | APCS-26 Coating (for Telecom) | IM21ZZ | 75 | 75 | 6 | M206428742A | M | 0
22 | Valid |  | Q.4 |  | STANCHION PIPE
23 | Valid |  |  |  |  | MATERIAL : HOT DIP GALVANIZED STEEL, 40 SCH WITH BASE PLATE, BLIND PLATE,
24 | Valid |  |  |  |  | NAMEPLATE BASE, EARTHING BOSS & GUSSET PLATE with APCS-26 coating
25 | Valid |  | Q.4.1 |  |  | Single pole Type | 2"x1600mm | 2"x1600mm | IM13ZZ |  |  |  | M206428747AY | EA | 0
26 | Valid |  | Q.4.2 |  |  | Single pole Type | 2"x700mm | 2"x700mm | IM13ZZ |  |  |  | M206428747O | EA | 0
27 | Valid |  | Q.4.3 |  |  | Single pole Type | 2"x2500mm | 2"x2500mm | IM13ZZ |  |  |  | M206428747AZ | EA | 0
28 | Valid |  | Q.4.4 |  |  | Double pole Type | 2"x1600mm | 2"x1600mm Double | IM13ZZ |  |  |  | M206428747BC | EA | 0
29 | Valid |  | Q.4.5 |  |  | Triple pole Type | 2"x1600mm | 2"x1600mm Triple | IM13ZZ |  |  |  | M206428747BD | EA | 0
30 | Valid |  | Q.4.6 |  |  | Multi Pole Type | 2"x1600mm | 2"x1600mm, TT Rack | IM13ZZ |  |  |  | M206428747BK | EA | 0
31 | Valid |  | Q.5 |  | STEEL PLATE
32 | Valid |  |  |  |  | MATERIAL : HOT DIP GALVANIZED STEEL
33 | Valid |  | Q.5.1 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 250 x 250 x 8t | 12mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 250 | 250 | 8 | M280954899C | EA | 0
34 | Valid |  | Q.5.2 |  |  | 12mmф x 2 Holes | 250 x 250 x 8t | 12mmф x 2 Holes | IM24ZZ | 250 | 250 | 8 | M280954899D | EA | 0
35 | Valid |  | Q.5.3 |  |  | 10mmф x 2 Holes (pre Fabricated) with APCS-26 Coating | 150 x 70 x 5t | 150 x 70 x 5t(base plate) + 250mm(Angle) plate) + 250mm(Angle), 10mmф x 2 Holes (pre Fabricated) with APCS-26 Coating | IM24ZZ | 150 | 70 | 5 | M349321990D | EA | 0
36 | Valid |  | Q.5.4 |  |  | 10mmф x 4 Holes with APCS-26 Coating | 100 x 100 x 5t | 10mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 100 | 100 | 5 | M280954901D | EA | 0
37 | Valid |  | Q.5.5 |  |  | (TOE Plate) with APCS-26 Coating | 125 x 2000 x 6t | (TOE Plate) with APCS-26 Coating | IM24ZZ | 125 | 2000 | 6 | M349321991B | EA | 0
38 | Valid |  | Q.5.6 |  |  | (Gusset Plate) with APCS-26 Coating | 130 x 80 x 5t | (Gusset Plate) with APCS-26 Coating | IM24ZZ | 130 | 80 | 5 | M365749317B | EA | 0
39 | Valid |  | Q.5.7 |  |  | (Name Plate Base) with APCS-26 Coating | 85 x 50 x 3t | (Name Plate Base) with APCS-26 Coating | IM24ZZ | 85 | 50 | 3 | M365749318B | EA | 0
40 | Valid |  | Q.5.8 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 400 x 210 x 6t | 12mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 400 | 210 | 6 | M367575867A | EA | 0
41 | Valid |  | Q.5.9 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 250 x 250 x 8t | 12mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 250 | 250 | 8 | M280954899E | EA | 0
42 | Valid |  | Q.5.10 |  |  | 10mmф x 4 Holes with APCS-26 Coating | 100 x 100 x 5t | 10mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 100 | 100 | 5 | M280954901E | EA | 0
43 | Valid |  | Q.5.11 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 350 x 350 x 10t | 12mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 350 | 350 | 10 | M206428755A | EA | 0
44 | Valid |  | Q.5.12 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 125 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 250 | 125 | 8 | M365749316B | EA | 1000 |  |  | 1000
45 | Valid |  | Q.5.13 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 70 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 250 | 70 | 8 | M414586712A | EA | 0
46 | Valid |  | Q.5.14 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 200 x 70 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 200 | 70 | 8 | M414586713A | EA | 0
47 | Valid |  | Q.5.15 |  |  | (TOE PLATE) with APCS-26 Coating | 350 x 125 x 6t | (TOE PLATE) with APCS-26 Coating | IM24ZZ | 350 | 125 | 6 | M414586721A | EA | 0
48 | Valid |  | Q.5.16 |  |  | (POST PLATE) 14 mmф x 2 Holes with APCS-26 Coationg | 100 x 200 x 6t x 82 x 90 x 6 | (POST PLATE) with APCS-26 Coating | IM24ZZ | 100 | 50 | 6 | M421387021A | EA | 0
49 | Valid |  | Q.5.17 |  |  | (TOE Plate) with APCS-26 Coating | 125 x 2000 x 6t | (TOE Plate) with APCS-26 Coating (for Telecom) | IM24ZZ | 125 | 2000 | 6 | M349321991C | EA | 0
50 | Valid |  | Q.5.18 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 125 x 8t | 12mmф x 2 Holes with APCS-26 Coating for Telecom | IM24ZZ | 250 | 125 | 8 | M365749316C | EA | 0
51 | Valid |  | Q.6 |  | SUNSHADE
52 | Valid |  | Q.6.1 |  |  | GRP, Bracket w/ 2" U-Bolt & Nuts, washer | NONE | GRP, Bracket w/ 2" U-Bolt & Nuts, washer, by Vendor | IM12ED |  |  |  | M349321992G | EA | 0
53 | Valid |  | Q.6.2 |  |  | GRP, (for Multi Transmitter Rack) with Bolting type | NONE | GRP, (for Multi Transmitter Rack) with Bolting type, by Vendor | IM12ED |  |  |  | M349321992H | EA | 0
54 | Valid |  | Q.6.3 |  |  | 316SS, Bracket w/ 2" U-Bolt & Nuts, washer | NONE | 316SS, Bracket w/ 2" U-Bolt & Nuts, washer, by Vendor | IM12ED |  |  |  | M349321992I | EA | 0
55 | Valid |  | Q.7 |  | NAME PLATE
56 | Valid |  |  |  |  | PHENOLIC / BAKELITE-LAMINATED PLASTIC WITH SCREWS (316SS)
57 | Valid |  | Q.7.1 |  |  | - BLACK TEXT WITH WHITE BACKGROUND FOR DCS | NONE | - BLACK TEXT WITH WHITE BACKGROUND FOR DCS | IM62ZZ |  |  |  | M220651966E | EA | 0
58 | Valid |  | Q.7.2 |  |  | - WHITE TEXT WITH RED BACKGROUND FOR ESD & FGS | NONE | - WHITE TEXT WITH RED BACKGROUND FOR ESD & FGS | IM62ZZ |  |  |  | M220651966F | EA | 0
59 | Valid |  | Q.7.3 |  |  | STAINLESS STEEL NAMEPLATE WITH BLACK TEXT FOR TAPPING POINT | NONE | STAINLESS STEEL NAMEPLATE WITH BLACK TEXT FOR TAPPING POINT | IM62ZZ |  |  |  | M220651966G | EA | 0
60 | Valid |  | Q.7.4 |  |  | TWISTED STAINLESS STEEL WIRE | NONE | TWISTED STAINLESS STEEL WIRE | IM62ZZ |  |  |  | M220651966H | EA | 0
61 | Valid |  | Q.8 |  | THREADED ROD
62 | Valid |  |  |  |  | MATERIAL : 316SS
63 | Valid |  | Q.8.1 |  |  | - 2 HEX HEAD 2 NUT & WASHER | NONE | - 2 HEX HEAD 2 NUT & WASHER | IM99EB |  |  |  | M349322107C | EA | 0
64 | Valid |  | Q.8.2 |  |  | - 2 HEX HEAD 2 NUT & WASHER | NONE | - 2 HEX HEAD 2 NUT & WASHER (for Telecom) | IM99EB |  |  |  | M349322107E | EA | 0
65 | Valid |  | Q.9 |  | THREADED ROD COUPLING
66 | Valid |  | Q.9.1 |  |  | MATERIAL : 316SS | NONE | MATERIAL : 316SS | IM99EB |  |  |  | M349322107D | EA | 0
67 | Valid |  | Q.9.2 |  |  | MATERIAL : 316SS | NONE | MATERIAL : 316SS (for Telecom) | IM99EB |  |  |  | M349322107F | EA | 0
68 | Valid |  | Q.10 |  | HILTI FASTNER W/NUTS
69 | Valid |  | Q.10.1 |  |  | 316SS, X-BT-R | NONE | 316SS, X-BT-R | IM41EA |  |  |  | M206340618GI | SET | 0
70 | Valid |  | Q.10.2 |  |  | 316SS, X-BT-R | NONE | 316SS, X-BT-R (for Telecom) | IM41EA |  |  |  | M206340618TC | SET | 0
71 | Valid |  | Q.11 |  | HILTI EXTEND ADAPTOR
72 | Valid |  | Q.11.1 |  |  | Item no. 387224 | NONE | Item no. 387224 | IM41EA |  |  |  | M206340618GJ | SET | 0
73 | Valid |  | Q.12 |  | SPACER for DUCT BANK
74 | Valid |  | Q.12.1 |  |  | CONDUIT 150mm BASE SPACERS | NONE | 6" BASE | IM99ZZ |  |  |  | M206396958HG | EA | 0
75 | Valid |  | Q.12.2 |  |  | CONDUIT 150mm INTERMEDIATE SPACERS | NONE | 6" INTERMEDIATE | IM99ZZ |  |  |  | M206396958HH | EA | 0
76 | Valid |  | Q.12.3 |  |  | CONDUIT 100mm BASE SPACERS | NONE | 4" BASE (forTelecom) | IM99ZZ |  |  |  | M206396958KX | EA | 0
77 | Valid |  | Q.12.4 |  |  | CONDUIT 100mm INTERMEDIATE SPACERS | NONE | 4" INTERMEDIATE (for Telecom) | IM99ZZ |  |  |  | M206396958KY | EA | 0
78 | Valid |  | Q.13 |  | END BELL (BELLMOUSE)
79 | Valid |  | Q.13.1 |  |  | Fitting for NEMA TC8 TYPE PVC conduit shall be in accordance with NEMA TC9, Color Grey | NONE | Fitting for NEMA TC8 TYPE PVC conduit shall be in accordance with NEMA TC9, Color Grey | IM99ZZ |  |  |  | M206396958FN | EA | 0
80 | Valid |  | Q.13.2 |  |  | Fitting for NEMA TC2 Type PVC conduit shall be in accordance with NEMA TC3, Color Grey | NONE | Fitting for NEMA TC2 Type PVC conduit shall be in accordance with NEMA TC3, Color Grey | IM99ZZ |  |  |  | M206396958FM | EA | 0
81 | Valid |  | Q.14 |  | End PLUG for PVC Conduit (Rubber PLUG for PVC Conduit) (FOR TELECOM DUCT BANK)
82 | Valid |  | Q.14.1 |  |  |  | NONE | END PLUG FOR 4" for Telecom | IM15ZZ |  |  |  | M206327315D | EA | 0
83 | Valid |  | Q.14.2 |  |  |  | NONE | END PLUG FOR 6" | IM15ZZ |  |  |  | M206327315C | EA | 0
84 | Valid |  | Q.15 |  | Quadplex Duct Plug for Sub-duct (FOR TELECOM DUCT BANK)
85 | Valid |  | Q.15.1 |  |  |  | NONE | Duct plug for 4" | IM99ZZ |  |  |  | M206396958HJ | EA | 0
86 | Valid |  | Q.16 |  | Simplex Sub Duct Plug (FOR TELECOM DUCT BANK)
87 | Valid |  | Q.16.1 |  |  |  | NONE | Duct plug for 1" (for Telecom) | IM99ZZ |  |  |  | M206396958KZ | EA | 0
88 | Valid |  | Q.17 |  | EARTH BOSS
89 | Valid |  |  |  |  | HOT DIP GALVANIZED STEEL, APCS-26 Coating
90 | Valid |  | Q.17.1 |  |  | (pre-welded at Stanchion pipe and else to be supplied separately for site installation.) | NONE | 30mmф x 30mm(L) x M12 | IM99ZZ |  |  |  | M206396958FU | EA | 0
91 | Valid |  | Q.18 |  | PULL BOX FOR TELECOM
92 | Valid |  | Q.18.1 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 100mmx405mmx75mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789A | EA | 0
93 | Valid |  | Q.18.2 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 150mmx510mmx75mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789B | EA | 0
94 | Valid |  | Q.18.3 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 102mmx102mmx54mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789C | EA | 285 | [6 empty] | 98 | 90 |  |  | 97
95 | Valid |  | Q.18.4 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 200mm x 686 mm x 75 mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789D | EA | 0
96 | Valid |  | Q.18.5 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 250mm x 686 mm x 75 mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789E | EA | 0
97 | Valid |  | Q.19 |  | CABLE MARKER POST (FOR TELECOM CABLE)
98 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036897-001
99 | Valid |  |  |  |  | - FIBER GLASS, ORANGE COLOR
100 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
101 | Valid |  |  |  |  | - 120mm x 100mm x 1400mm
102 | Valid |  | Q.19.1 |  |  |  | NONE | TE, POST, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186X | EA | 0
103 | Valid |  | Q.19.2 |  |  |  | NONE | TE, POST, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186Y | EA | 0
104 | Valid |  | Q.19.3 |  |  |  | NONE | TE, POST, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186Z | EA | 0
105 | Valid |  | Q.19.4 |  |  |  | NONE | TE, POST, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AA | EA | 0
106 | Valid |  | Q.19.5 |  |  |  | NONE | TE, POST, SIGN TYPE "E" | IM35ZZ |  |  |  | M201587186AB | EA | 0
107 | Valid |  | Q.19.6 |  |  |  | NONE | MARKER POST | IM35ZZ |  |  |  | M201587186AT | EA | 0
108 | Valid |  | Q.20 |  | SURFACE MARKER (FOR TELECOM CABLE)
109 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036273-001
110 | Valid |  |  |  |  | - CONCRETE SLAB
111 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
112 | Valid |  |  |  |  | - 305mm x 305mm x 76mm
113 | Valid |  | Q.20.1 |  |  |  | NONE | TE, MARKER, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AC | EA | 0
114 | Valid |  | Q.20.2 |  |  |  | NONE | TE, MARKER, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AD | EA | 0
115 | Valid |  | Q.20.3 |  |  |  | NONE | TE, MARKER, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AE | EA | 0
116 | Valid |  | Q.20.4 |  |  |  | NONE | TE, MARKER, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AF | EA | 0
117 | Valid |  | Q.20.5 |  |  |  | NONE | CONCRETE SLAB | IM35ZZ |  |  |  | M201587186N | EA | 0
118 | Valid |  | Q.21 |  | WARNING TAPE (FOR TELECOM CABLE)
119 | Valid |  |  |  |  | - ORANGE COLOR
120 | Valid |  | Q.21.1 |  |  | DETECTABLE MARKER TAPE | NONE | TE, DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AG | m | 0
121 | Valid |  | Q.21.2 |  |  | NON-DETECTABLE MARKER TAPE | NONE | TE, NON-DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AH | m | 0
122 | Valid |  | Q.22 |  | CABLE MARKER POST (FOR INSTRUMENT CABLE)
123 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036326-001
124 | Valid |  |  |  |  | - RED WOOD
125 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
126 | Valid |  |  |  |  | - 100mm x 100mm x 1370mm
127 | Valid |  | Q.22.1 |  |  |  | NONE | CI, POST, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AI | EA | 0
128 | Valid |  | Q.22.2 |  |  |  | NONE | CI, POST, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AJ | EA | 0
129 | Valid |  | Q.22.3 |  |  |  | NONE | CI, POST, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AK | EA | 0
130 | Valid |  | Q.22.4 |  |  |  | NONE | SIGN-POST | IM35ZZ |  |  |  | M201587186BN | EA | 0
131 | Valid |  | Q.23 |  | SURFACE MARKER (FOR INSTRUMENT CABLE)
132 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036273-001
133 | Valid |  |  |  |  | - CONCRETE SLAB
134 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
135 | Valid |  |  |  |  | - 305mm x 305mm x 76mm
136 | Valid |  | Q.23.1 |  |  |  | NONE | CI, MARKER, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AL | EA | 0
137 | Valid |  | Q.23.2 |  |  |  | NONE | CI, MARKER, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AM | EA | 0
138 | Valid |  | Q.23.3 |  |  |  | NONE | CI, MARKER, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AN | EA | 0
139 | Valid |  | Q.23.4 |  |  |  | NONE | CI, MARKER, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AO | EA | 0
140 | Valid |  | Q.23.5 |  |  |  | NONE | CABLE MARKER(PLAQUE) | IM35ZZ |  |  |  | M201587186BO | EA | 0
141 | Valid |  | Q.24 |  | WARNING TAPE (FOR INSTRUMENT CABLE)
142 | Valid |  |  |  |  | - YELLOW COLOR
143 | Valid |  | Q.24.1 |  |  | DETECTABLE MARKER TAPE | NONE | CI, DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AP | M | 0
144 | Valid |  | Q.24.2 |  |  | NON-DETECTABLE MARKER TAPE | NONE | CI, NON-DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AQ | M | 0
145 | Valid |  | Q.25 |  | ELECTRONINC MARKER SYSTEM (FOR TELECOM CABLE)
146 | Valid |  | Q.25.1 |  |  | ELECTRONINC MARKER SYSTEM | NONE | (for Telecom) | IM35ZZ |  |  |  | M201587186AS | EA | 0
Note on W99: HEC: 50 for Data outlet (assumed) 48 for Security (as per IFB drawing)
Note on X99: HEC: 50 for Data outlet (assumed) 40 for Security (as per IFB drawing)
Note on AA99: HEC: 50 for Data outlet (assumed) 47 for Security (as per IFB drawing)

## Telecom & Security System
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | Item | Description |  | Tag No | Material Master | Height | Core/Pair Number | Composition | MR No. | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[5 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[15 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | S | Telecommunication and Security | [5 empty] | 0 |  |  |  | 0
2 | Valid |  | S.1 | TELECOM SYSTMEM (IT) | [5 empty] | 0 |  |  |  | 0
3 | Valid |  | S.1.1 | Data Network System | [5 empty] | 0 |  |  |  | 0
4 | Valid |  | S.1.1.1 | Data Network System Rack | [5 empty] | 0 |  |  |  | 0
5 | Valid |  | S.1.1.1.1 | Data Network System Oepn Rack | 19" Open Frame Rack (42U) | 0 | S.1.1.1.1 | FI31CC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
6 | Valid |  | S.1.1.1.2 | Data Network System Wall Mount Rack | 19" Swing Gate Wall Mount Rack (14U): CUBE-IT | 0 | S.1.1.1.2 | FI31CB00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
7 | Valid |  | S.1.1.1.3 | Data Network System Ethernet Switch | Layer 2 (Layer 3 compatible) LAN Access Switches (with PoE+ capability) |  | S.1.1.1.3 |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
8 | Valid |  | S.1.1.1.3.1 | Data Network System 24 port Ethernet Switch | 24 port Ethernet Switch | 0 | S.1.1.1.3.1 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
9 | Valid |  | S.1.1.1.3.2 | Data Network System 48 port Modular type Ethernet Switch | 48 port Modular type Ethernet Switch | 0 | S.1.1.1.3.2 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
10 | Valid |  | S.1.1.1.3.3 | Data Network System 48 port Ethernet Switch | 48 port Ethernet Switch | 0 | S.1.1.1.3.3 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
11 | Valid |  | S.1.1.1.3.4 | Data Network System 72 port Modular Ethernet Switch | 72 port Modular Ethernet Switch | 0 | S.1.1.1.3.4 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
12 | Valid |  | S.1.1.1.3.5 | Data Network System 144 port Modular type Ethernet switch | 108 port Modular type Ethernet switch | 0 | S.1.1.1.3.5 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
13 | Valid |  | S.1.1.1.4 | Data Network System SFP Transceiver for switch | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.1.1.4 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
14 | Valid |  | S.1.1.1.5 | Data Network System SFP+ Transceiver for switch | 10G SFP+ LC LR SMF transciever for Aruba switch | 0 | S.1.1.1.5 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
15 | Valid |  | S.1.1.1.6 | Data Network System SFP Transceiver for router | 1G SFP LC LX SMF transciever for Juniper PE router | 0 | S.1.1.1.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
16 | Valid |  | S.1.1.1.7 | Data Network System SFP+ Transceiver for router | 10G SFP+ LC LR SMF transciever for Juniper PE router | 0 | S.1.1.1.7 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
17 | Valid |  | S.1.1.1.8 | Data Network System Power Receptacles | 230VAC, 20A, duplex | 0 | S.1.1.1.8 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
18 | Valid |  | S.1.1.1.9 | Data Network System Fiber Optic Patch Panel |  |  | S.1.1.1.9 |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
19 | Valid |  | S.1.1.1.9.1 | Data Network System 24 Port Fiber Optic Patch Panel | 24 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.1 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
20 | Valid |  | S.1.1.1.9.2 | Data Network System 48 Port Fiber Optic Patch Panel | 48 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
21 | Valid |  | S.1.1.1.9.3 | Data Network System 144 Port Fiber Optic Patch Panel | 144 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.1.1.1.9.4 | Data Network System 12 Port Fiber Optic Patch Panel | 12 Port Fiber Optic Patch Panel |  | S.1.1.1.9.4 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.1.1.1.9.5 | Data Network System 6 Port Fiber Optic Patch Panel | 6 Port Fiber Optic Patch Panel |  | S.1.1.1.9.5 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.1.1.1.9.6 | Data Network System 96 Port Fiber Optic Patch Panel | 96 Port Fiber Optic Patch Panel |  | S.1.1.1.9.6 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
22 | Valid |  | S.1.1.1.10 | Data Network System UTP Patch Panel | including Front RJ45 'Snap-in' type connectors with clear plastic indetification labels |  | S.1.1.1.10 |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
23 | Valid |  | S.1.1.1.10.1 | Data Network System 24 Port UTP Patch panel | 24 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.1 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
24 | Valid |  | S.1.1.1.10.2 | Data Network System 48 Port UTP Patch panel | 48 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
25 | Valid |  | S.1.1.1.10.3 | Data Network System 72 Port UTP Patch panel | 72 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
26 | Valid |  | S.1.1.2 | Data Network System Uninterruptible Power Supply(UPS) | Rack mountable type with a minimum of 2 hours UPS autonomy |  | S.1.1.2 |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
27 | Valid |  | S.1.1.2.1 | Data Network System Rack mountable ATS (Auotomatic Tranfer Switch) | ATS | 0 | S.1.1.2.1 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
28 | Valid |  | S.1.1.2.2 | Data Network System 3kVA UPS | 3kVA UPS | 0 | S.1.1.2.2 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
29 | Valid |  | S.1.1.2.3 | Data Network System 5kVA UPS | 3.5kVA UPS | 0 | S.1.1.2.3 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
30 | Valid |  | S.1.1.2.4 | Data Network System 8kVA UPS | 8kVA UPS | 0 | S.1.1.2.4 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
31 | Valid |  | S.1.1.2.5 | Data Network System 10kVA UPS | 10kVA UPS | 0 | S.1.1.2.5 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
32 | Valid |  | S.1.1.2.6 | Data Network System Battery Packs | Battery Pack for 3kVA UPS | 0 | S.1.1.2.6 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
33 | Valid |  | S.1.1.2.7 | Data Network System Battery Packs | Battery Pack for 3.5kVA UPS | 0 | S.1.1.2.7 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
34 | Valid |  | S.1.1.2.8 | Data Network System Battery Packs | Battery Pack for 10kVA UPS | 0 | S.1.1.2.8 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
35 | Valid |  | S.1.1.3 | Data Network System Patch Cords | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
36 | Valid |  | S.1.1.3.1 | Data Network System UTP Patch cord (1.5m) | UTP Patch cord (1.5m), Cat.6A | 0 | S.1.1.3.1 | FI37HC02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
37 | Valid |  | S.1.1.3.2 | Data Network System Fiber Optic Patch cord (1.5m) | Fiber Optic Patch cord (1.5m) | 0 | S.1.1.3.2 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
38 | Valid |  | S.1.1.3.3 | Data Network System Fiber Optic Patch cord (15m) | Fiber Optic Patch cord (15m) | 0 | S.1.1.3.3 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
39 | Valid |  | S.1.1.4 | Data Network System Telecom enclosure with switch | for PSA FOC Splice |  |  |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
40 | Valid |  | S.1.1.4.1 | Data Network System Ethernet switch | Ethernet Switch (24 port) if any | 0 | S.1.1.4.1 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
41 | Valid |  | S.1.1.4.2 | Data Network System SFP Transceiver | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.1.4.2 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
42 | Valid |  | S.1.1.4.3 | Data Network System Fiber Optic Patch Panel (DIN, 4port) | Fiber Optic Patch Panel (Rac Mount, 12port) | 0 | S.1.1.4.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
43 | Valid |  | S.1.1.4.4 | Data Network System Fiber Optic Patch Panel (DIN, 4port) | Fiber Optic Patch Panel (Rac Mount, 24port) | 0 | S.1.1.4.4 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
44 | Valid |  | S.1.1.4.5 | Data Network System Telecom enclosure | Telecom enclosure Size: 1525h x 575w x 300d | 0 | S.1.1.4.5 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
45 | Valid |  | S.1.1.4.6 | Data Network System Cat.6 Surge Protector | Cat.6 Surge Protecto (8port, DIN) | 0 | S.1.1.4.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
46 | Valid |  | S.1.1.4.7 | Data Network System Cat.6 Surge Protector | Thin Cabinet for Telecom | 0 | S.1.1.4.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
47 | Valid |  | S.1.2 | Telephone System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
48 | Valid |  | S.1.2.1 | Telephone System Basic VOIP Telephone Handset | Basic VOIP Telephone Handset | 0 | S.1.2.1 | FI33EF11ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
49 | Valid |  | S.1.2.2 | Telephone System Manager VOIP Telephone Handset | Manager VOIP Telephone Handset | 0 | S.1.2.2 | FI33EF12ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
50 | Valid |  | S.1.2.3 | Telephone System Secretary IP Telephone handset | Secretary IP Telephone handset | 0 | S.1.2.3 | FI33EF12ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
51 | Valid |  | S.1.2.4 | Telephone System Meeting Room IP Conference Telephone handsets | Meeting Room IP Conference Telephone handsets | 0 | S.1.2.4 | FI33EF13ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
52 | Valid |  | S.1.2.5 | Telephone System VOIP Gateway | For Analoge Telephone to IP | 0 | S.1.2.5 | FI33EI00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.1.2.6 | Telephone System Basic Wall Mount IP Telephone | Weatherproof Type | [6 empty] | BOTB-PKG2-MR-TE-0001 | SETS | 0
53 | Valid |  | S.1.3 | pLTE Radio System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
54 | Valid |  | S.1.3.1 | Indoor Radio Repeating System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
55 | Valid |  | S.1.3.1.1 | Indoor Radio Repeating System Indoor Radio Repearter | Small Cell / eNodeB | 0 | S.1.3.1.1 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
56 | Valid |  | S.1.3.1.2 | Indoor Radio Repeating System LTE Indoor antenna | Repeating Antenna | 0 | S.1.3.1.2 | FI36GE11ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
57 | Valid |  | S.1.3.1.3 | Indoor Radio Repeating System Coaxial 2 Way Splitter | Coaxial 2 Way Splitter | 0 | S.1.3.1.3 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
58 | Valid |  | S.1.3.1.4 | Indoor Radio Repeating System Coaxial Cable 1/2" | Coaxial Cable 1/2" | 0 | S.1.3.1.4 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
59 | Valid |  | S.1.3.1.5 | Indoor Radio Repeating System Fiber Optic patch cord(15m) | Fiber Optic Patch cord (SC/APC, 15m) | 0 | S.1.3.1.5 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
60 | Valid |  | S.1.3.1.6 | Indoor Radio Repeating System Fiber Optic patch cord(10m) | Fiber Optic Patch cord (SC/APC, 10m) | 0 | S.1.3.1.6 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
61 | Valid |  | S.1.3.1.7 | Indoor Radio Repeating System Power cord(10m) | Power cord (10m) | 0 | S.1.3.1.7 | FI37HG02ZZ-0000001 | 0 | 2 | C | BOTB-PKG2-MR-TE-0001 | SETS | 0
62 | Valid |  | S.1.3.1.8 | Indoor Radio Repeating System DC Block | DC Block | 0 | S.1.3.1.8 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
63 | Valid |  | S.1.3.1.9 | Indoor Radio Repeating System Attenuator | 10dB Attenuator | 0 | S.1.3.1.9 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
64 | Valid |  | S.1.3.1.9.2 | Indoor Radio Repeating System Attenuator | 3dB Attenuator | 0 | S.1.3.1.9.2 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
65 | Valid |  | S.1.3.1.9.3 | Indoor Radio Repeating System Attenuator | 6dB Attenuator | 0 | S.1.3.1.9.3 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
66 | Valid |  | S.1.3.1.10 | Indoor Radio Repeating System SFP Transceiver | SFP Transceiver | 0 | S.1.3.1.10 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
67 | Valid |  | S.1.3.1.11 | Indoor Radio Repeating System SFP Transceiver | 12 SC/APC Simpled Splicing Casette | 0 | S.1.3.1.11 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
68 | Valid |  | S.1.3.1.12 | Accessorfies for Indoor Repater System | 272 NM, 42 NF, 21 DM Connectors and 72 Mounting Plates | 0 | S.1.3.1.12 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | Lot | 0
69 | Valid |  | S.1.3.1.13 | Indoor Radio Repeating System 6dB Tapper | 6dB Tapper | 0 | S.1.3.1.13 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
70 | Valid |  | S.1.3.1.14 | Indoor Radio Repeating System 8dB Tapper | 8dB Tapper | 0 | S.1.3.1.14 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
71 | Valid |  | S.1.3.1.15 | Indoor Radio Repeating System 10dB Tapper | 10dB Tapper | 0 | S.1.3.1.15 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
72 | Valid |  | S.1.3.1.16 | Indoor Radio Repeating System 15dB Tapper | 15dB Tapper | 0 | S.1.3.1.16 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
73 | Valid |  | S.1.3.2 | Portable Radio System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
74 | Valid |  | S.1.3.2.1 | Portable Radio System Handheld Portable Radio | Handheld Portable Radio | 0 | S.1.3.2.1 | FI36GH00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
75 | Valid |  | S.1.3.2.2 | Portable Radio System Vehicle Mounted Radio | Vehicle Mounted Radio | 0 | S.1.3.2.2 | FI36GH00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
76 | Valid |  | S.1.3.3 | Fixed Radio System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
77 | Valid |  | S.1.3.3.1 | Fixed Radio System LTE Desk-top Terminal | MCPTT-enabled | 0 | S.1.3.3.1 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
78 | Valid |  | S.1.3.3.2 | Fixed Radio System Radio Interface Unit | MCPTT Client Software | 0 | S.1.3.3.2 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
79 | Valid |  | S.1.3.3.3 | Fixed Radio System RRU(Remote Radio Unit) | Audio Interface Unit / USB Controller / Dispatch Console | 0 | S.1.3.3.3 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
80 | Valid |  | S.1.3.3.4 | Fixed Radio System Outdoor Antenna | LTE Outdoor MIMO Antenna (2x2 / 4x4) | 0 | S.1.3.3.4 | FI36GE11ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
81 | Valid |  | S.1.3.3.5 | Fixed Radio System Pole for Outdoor Antenna | Pole for Outdoor Antenna | 0 | S.1.3.3.5 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
82 | Valid |  | S.1.3.3.6 | Fixed Radio System Surge Protector for Antenna | Surge Protector for Antenna | 0 | S.1.3.3.6 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
83 | Valid |  | S.1.3.3.7 | Fixed Radio System 19" Open Frame Rack | 19" Open Frame Rack (if any) | 0 | S.1.3.3.7 | FI36GA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
84 | Valid |  | S.1.3.3.8 | Fixed Radio System Coaxial Cable 1/2" | LMR400 / 1/2” | 0 | S.1.3.3.8 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
85 | Valid |  | S.1.3.3.9 | Fixed Radio System Surge Protector Grounding Bracket | Grounding Kit (RF + Network) | 0 | S.1.3.3.9 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
86 | Valid |  | S.1.3.3.10 | Fixed Radio System Structured Cabling | Cat6A UTP | 0 | S.1.3.3.10 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
87 | Valid |  | S.1.3.3.11 | Fixed Radio System 24port Ethernet switch | L2/L3 Managed Switch (PoE optional) | 0 | S.1.3.3.11 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
88 | Valid |  | S.1.3.3.12 | Fixed Radio System Programming Kit | Device Management SW / SIM Provisioning Tool | 0 | S.1.3.3.12 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
89 | Valid |  | S.1.4 | Wireless LAN(WLAN) System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
90 | Valid |  | S.1.4.1 | Wireless LAN System Wireless Access Points | Wireless Access Points | 0 | S.1.4.1 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
91 | Valid |  | S.1.4.2 | Wireless LAN System Explosion Proof Wireless Access Points | Explosion Proof Wireless Access Points | 0 | S.1.4.2 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
92 | Valid |  | S.1.4.3 | Wireless LAN System Hi-POE Injector | For explosion proof WLAN access points | 0 | S.1.4.3 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
93 | Valid |  | S.1.5 | Industrial Wi-Fi SYSTEM | Wi-Fi 6 or above |  |  |  |  | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
94 | Valid |  | S.1.5.1 | Industrial Wi-Fi SYSTEM Industrial Wi-Fi access points | Industrial Wi-Fi access points | 0 | S.1.5.1 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
95 | Valid |  | S.1.5.2 | Industrial Wi-Fi SYSTEM Explosion proof Industrial Wi-Fi access point | Explosion proof Industrial Wi-Fi access point | 0 | S.1.5.2 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
96 | Valid |  | S.1.5.3 | Industrial Wi-Fi SYSTEM External Antenna for WIFI access point | External Antenna for WIFI access point | 0 | S.1.5.3 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
97 | Valid |  | S.1.5.4 | Industrial Wi-Fi SYSTEM WIFI antenna extension cable | WIFI antenna extension cable | 0 | S.1.5.4 | FI37HG01ZZ-0000001 | 0 | 2 | C | BOTB-PKG2-MR-TE-0001 | M | 0
98 | Valid |  | S.1.5.5 | Industrial Wi-Fi SYSTEM 2m Pole for Antenna for WIFI | 2m Pole for Antenna for WIFI | 0 | S.1.5.5 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
99 | Valid |  | S.1.5.6 | Industrial Wi-Fi SYSTEM 7m Pole for Antenna for WIFI | 6m Pole for Antenna for WIFI, ASCE-7-05, 155km/h | 0 | S.1.5.6 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
100 | Valid |  | S.1.5.6.1 | Industrial Wi-Fi SYSTEM 6m Pole for Explosion Antenna for WIFI | 6m Pole for Antenna for WIFI, ASCE-7-05, 155km/h | 0 | S.1.5.6.1 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
101 | Valid |  | S.1.5.7 | Industrial Wi-Fi SYSTEM Cat.6A surge protector | Cat.6A surge protector | 0 | S.1.5.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
102 | Valid |  | S.1.5.8 | Industrial Wi-Fi SYSTEM Enclousure for Industrial Ethernet Switch | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
103 | Valid |  | S.1.5.8.1 | Industrial Wi-Fi SYSTEM Industrial Ethernet Switch (4 port) | POE Injector (Normal Installation) | 0 | S.1.5.8.1 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
104 | Valid |  | S.1.5.8.2 | Industrial Wi-Fi SYSTEM Explosion proof Industrial Ethernet Switch (4 port) | POE Injector (Hazard Area Installation) | 0 | S.1.5.8.2 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
105 | Valid |  | S.1.5.8.3 | Industrial Wi-Fi SYSTEM Enclousure | Enclousure (400 x 400 x 100) | 0 | S.1.5.8.3 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
106 | Valid |  | S.1.5.8.4 | Industrial Wi-Fi SYSTEM Explosion proof Enclousure | Explosion proof Enclousure (400 x 400 x 100) | 0 | S.1.5.8.4 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
107 | Valid |  | S.1.5.8.5 | Industrial Wi-Fi SYSTEM SFP Transceiver for switch | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.5.8.5 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
108 | Valid |  | S.1.5.8.6 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | 1G SFP LC LX SMF transciever for WIFI AP | 0 | S.1.5.8.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
109 | Valid |  | S.1.5.8.7 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | Outdoor Rated FO Patch cord(5m) | 0 | S.1.5.8.7 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
110 | Valid |  | S.1.5.8.8 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | Outdoor Rated UTP Patch cord(5m) | 0 | S.1.5.8.8 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
111 | Valid |  | S.1.6 | Structural Cabling System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
112 | Valid |  | S.1.6.1 | Structural Cabling System LAN outlet | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
113 | Valid |  | S.1.6.1.1 | Structural Cabling System Three(3) port Cat.6A LAN outlet / Wall mount | Three(3) port Cat.6A LAN outlet / Wall mount | 0 | S.1.6.1.1 | FI31CD02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
114 | Valid |  | S.1.6.1.2 | Structural Cabling System Two(2) port Cat.6A LAN outlet / Wall mount | Two(2) port Cat.6A LAN outlet / Wall mount | 0 | S.1.6.1.2 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 75 | [6 empty] | 6 | 52 |  |  | 5 | 6 | 6
115 | Valid |  | S.1.6.1.3 | Structural Cabling System Floor Box with Two(2) port Cat.6A LAN outlet | Floor Box with Two(2) port Cat.6A LAN outlet | 0 | S.1.6.1.3 | FI31CD02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
116 | Valid |  | S.1.6.1.4 | Structural Cabling System Two(2) port Cat.6A LAN outlet / Ceiling mount | Two(2) port Cat.6A LAN outlet / Ceiling mount | 0 | S.1.6.1.4 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 27 | [6 empty] | 5 | 8 |  |  | 4 | 5 | 5
117 | Valid |  | S.1.6.1.5 | Structural Cabling System, Floor box with 2 receptacles | with Floor Box | 0 | S.1.6.1.5 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
118 | Valid |  |  | TELECOM SYSTMEM (NON-IT) | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
119 | Valid |  | S.2 | In-Plant Voice Paging System (IVPS) | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
120 | Valid |  | S.2.1 | Paging System Main Cabinet | Main Cabinet | 0 | S.2.1 | FI32DA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
121 | Valid |  | S.2.2 | Paging System Local Cabinet | Local Cabinet | 0 | S.2.2 | FI32DB00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
122 | Valid |  | S.2.3 | Paging System PAGA Workstation with accessories | PAGA Workstation with accessories | 0 | S.2.3 | FI32DC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
123 | Valid |  | S.2.4 | Paging System Operator Access Panel | Access Control Panel | 0 | S.2.4 | FI32DD00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
124 | Valid |  | S.2.5 | Paging System Indoor Ceiling Speaker with Junction Box | Indoor Ceiling Speaker | 0 | S.2.5 | FI32DE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
125 | Valid |  | S.2.6 | Paging System LoudSpeaker (Box type) with Junction Box | LoudSpeaker (Box type) | 0 | S.2.6 | FI32DF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
126 | Valid |  | S.2.7 | Paging System Loudspeaker(Horn Type) with Junction Box | General Purpose | 0 | S.2.7 | FI32DG00AA-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
127 | Valid |  | S.2.8 | Paging System Loudspeaker(Horn Type) with Junction Box | Weather proof | 0 | S.2.8 | FI32DG00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
128 | Valid |  | S.2.9 | Paging System Loudspeaker(Horn Type) with Junction Box | Explosion Proof | 0 | S.2.9 | FI32DG00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
129 | Valid |  | S.2.10 | Paging System Distribution Junction Box | General Purpose | 0 | S.2.10 | FI32DJ00AA-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
130 | Valid |  | S.2.11 | Paging System Distribution Junction Box | Weather proof ( Multi JB ) | 0 | S.2.11 | FI32DJ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
131 | Valid |  | S.2.12 | Paging System Distribution Junction Box | Explosion Proof ( Multi JB ) | 0 | S.2.12 | FI32DJ00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
133 | Valid |  | S.2.14 | Paging System Intercom Station With Acoustic Booth | Intercom Station With Acoustic Booth | 0 | S.2.14 | FI32DM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.14 | Paging System Intercom Station With Acoustic Booth | Intercom Station With Acoustic Booth (WP) | [7 empty] | SETS | 0
134 | Valid |  | S.2.15 | Paging System Flash Beacon | General Purpose | 0 | S.2.15 | FI32DN00AA-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
132 | Valid |  | S.2.13 | Paging System Intercom Station with Junction Box | Intercom Station with amplifier | 0 | S.2.13 | FI32DL00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
135 | Valid |  | S.2.16 | Paging System Flash Beacon | Weather proof | 0 | S.2.16 | FI32DN00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
136 | Valid |  | S.2.17 | Paging System Flash Beacon with Junction Box | Explosion Proof | 0 | S.2.17 | FI32DN00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
137 | Valid |  | S.2.18 | Paging System Speaker Pole | Speaker Pole up to 3m | 0 | S.2.18 | FI32DO00ZZ-0000001 | 3 | 0 | 0 | BOTB-PKG2-MR-TE-0001 | SETS | 0
138 | Valid |  | S.2.19 | Paging System Speaker Pole | Speaker Pole 3m - 8m Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101V | 0 | S.2.19 | FI32DO00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
139 | Valid |  | S.2.20 | Paging System Speaker Pole | Speaker Pole 8m - 15m | 0 | S.2.20 | FI32DO00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
140 | Valid |  | S.2.21 | Paging System Existing Interface software/license | Existing Interface software/license |  | S.2.21 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.22 | Paging Remote Amplifiers | 20W, 8ohms/16ohms Indoor |  | S.2.22 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.23 | Paging Remote Amplifiers | 20W, 8ohms/16ohms Outdoor |  | S.2.23 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  |  | Paging Remote Amplifiers (Explosion proof) | 20W, 8ohms/16ohms Outdoor | [7 empty] | SETS | 0
|  |  | S.2.24 | Paging System Cables | 2C Unarmoured |  | S.2.24 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.25 | Paging System Cables | 16C Unarmoured |  | S.2.25 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.26 | Paging System Cables | 2C Armoured |  | S.2.26 | FI32DP00ZZ-0000002 |  | 1 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
|  |  | S.2.27 | Paging System Cables | 16C Armoured |  | S.2.27 | FI32DP00ZZ-0000003 |  | 2 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
141 | Valid |  | S.3 | Emergency Siren System |  |  | S.3 | FZ75ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
142 | Valid |  | S.3.1 | Siren System Cabinet | 19" Cabinet |  | S.3.1 | FZ76ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
143 | Valid |  | S.3.2 | Siren System Operator Access Panel | Operator Access Panel |  | S.3.2 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
144 | Valid |  | S.3.3 | Omni-directional modularot high powered speaker array | 8 x 400W (3200W) Active Modules / 30 meters Siren Cable / Pole mount |  | S.3.3 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
145 | Valid |  | S.3.4 | Electronic Siren Controller Enclosure | Stainless steel , NEMA 4X |  | S.3.4 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
146 | Valid |  | S.3.5 | Charger, Batteries and Battery Enclosure | Stainless steel , NEMA 4X Battery & Battery Enclsure meets: SAES-T-151, SAES-P-103, 17-SAMSS-511, and IOGP S-740 |  | S.3.5 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
147 | Valid |  | S.3.6 | Flahing Beacon | Orange color |  | S.3.6 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
148 | Valid |  | S.3.7 | Flahing Beacon | Green color |  | S.3.7 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
149 | Valid |  | S.3.8 | Siren Tower | Height : 20M / Self-supporting, Ligtning protection, Maintenace Platform with ladders, Earthing and bonding Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101V |  | S.3.8 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
150 | Valid |  | S.3.9 | Siren System Pole | Pole |  | S.3.9 | FZ78ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
151 | Valid |  | S.3.10 | Workstation w/monitor |  |  | S.3.10 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
152 | Valid |  | S.5 | Communication System Others Telecom & Security System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
153 | Valid |  | S.5.1 | Communication System Others Telecom & Security System UPS - Cabinet Type | Telecom & Security System UPS - Cabinet Type | 0 | S.5.1 | FI37HA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
154 | Valid |  | S.5.2 | Communication System Others Patch panel | Patch panel for FIBER OPTIC | 0 | S.5.2 | FI37HB01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
155 | Valid |  | S.5.3 | Communication System Others Patch panel | Patch panel for UTP | 0 | S.5.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
156 | Valid |  | S.5.4 | Communication System Others Patch cord | Patch cord for Fiber OPTIC | 0 | S.5.4 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
157 | Valid |  | S.5.5 | Communication System Others Patch cord | Patch cord FOR UTP | 0 | S.5.5 | FI37HC02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
158 | Valid |  | S.5.6 | Communication System Others Junction Box | Junction Box | 0 | S.5.6 | FI37HD00AA-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
159 | Valid |  | S.5.7 | Communication System Others Junction Box | Junction Box (400 x 400 x 100 ) | 0 | S.5.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
160 | Valid |  | S.5.8 | Communication System Others Explosion proof junction Box | Explosion proof junction Box | 0 | S.5.8 | FI37HD00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
161 | Valid |  | S.5.9 | Communication System Others Printer | FAX | 0 | S.5.9 | FI37HE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
162 | Valid |  | S.5.10 | Communication System Others Printer | Printer | 0 | S.5.10 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
163 | Valid |  | S.5.11 | Communication System Others Coax Cable | Coax Cable 1/2" | 0 | S.5.11 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
164 | Valid |  | S.5.12 | Communication System Others Coax Cable | Coax Cable 7/8" | 0 | S.5.12 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
165 | Valid |  | S.5.13 | Communication System Others Special Cable (Vendor Supply) | Special Cable, Wifi Antenna extension (Vendor Supply) | 0 | S.5.13 | FI37HG01ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
166 | Valid |  | S.5.14 | Communication System Others Special Cable (Vendor Supply) | Special Cable, Pwer Cord (Vendor Supply) | 0 | S.5.14 | FI37HG02ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
167 | Valid |  | S.5.15 | Communication System Others PEDESTAL | PEDESTAL | 0 | S.5.15 | FI37HH00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
168 | Valid |  | S.5.16 | Communication System Others Miscellaneous | Miscellaneous | 0 | S.5.16 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
169 | Valid |  | S.6 | IT-ACS |  |  | S.6 |  |  | 0 |  |  |  | 0
170 | Valid |  | S.6.1 | ACS Controller |  |  | S.6.1 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
171 | Valid |  | S.6.2 | Power Supply |  |  | S.6.2 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
172 | Valid |  | S.6.3 | Door Contact |  |  | S.6.3 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
173 | Valid |  | S.6.4 | Electromagnetic Lock |  |  | S.6.4 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
174 | Valid |  | S.6.5 | Card Reader with Keypad |  |  | S.6.5 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
175 | Valid |  | S.6.6 | Request to Exit Button |  |  | S.6.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
176 | Valid |  | S.6.7 | Emergency Break Glass |  |  | S.6.7 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
177 | Valid |  | S.6.8 | Indoor Dome Camera |  |  | S.6.8 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
|  |  | S.6.9 | IT-ACS Server Upgrade and Licensing (Existing) |  |  | S.6.9 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | No. | 0
178 | Valid |  | S.7 | Intrusion Detection System for Category 1 Fence | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
179 | Valid |  | S.7.1 | IDAS Fixed CCTV Camera with JB and accessories | Fixed Camera with Bracket including license | 0 | S.7.1 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
180 | Valid |  | S.7.2 | IDAS PTZ CCTV Camera with JB and accessories | PTZ Camera with JB, Bracket including license | 0 | S.7.2 | FF19ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
181 | Valid |  | S.7.3 | IDAS Video Analytic Camera with JB and accessories - including license | Video Analytic Camera with Bracket including license | 0 | S.7.3 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
182 | Valid |  | S.7.4 | IDAS Camera Pole for fixed camera | Camera Pole 5m | 0 | S.7.4 | FF22ZZ00ZZ-0000001 | 5 | 0 | 0 | BOTB-PKG2-MR-TE-0001 | SETS | 0
183 | Valid |  | S.7.5 | IDAS Camera Pole for PTZ camera | Camera Pole 7m | 0 | S.7.5 | FF22ZZ00ZZ-0000001 | 7 | 0 | 0 | BOTB-PKG2-MR-TE-0001 | SETS | 0
184 | Valid |  | S.7.6 | IDAS MIDS SENSOR | Micro wave Transmitter with bracket | 0 | S.7.6 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
185 | Valid |  | S.7.7 | IDAS MIDS SENSOR | Micro wave Receiver with bracket | 0 | S.7.7 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
186 | Valid |  | S.7.8 | IDAS MIDS SENSOR | Micro wave Tranceiver with bracket | 0 | S.7.8 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
187 | Valid |  | S.7.9 | IDAS FOSS | Fiber Optic Fence Sensor Cable | 0 | S.7.9 | FR22BD00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | M | 0
188 | Valid |  | S.7.10 | IDAS FOSS | Fiber Break-out Box including all component | 0 | S.7.10 | FR21AC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
189 | Valid |  | S.7.11 | IDAS OTHERS | Magnetic Bodning Sensor | 0 | S.7.11 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
190 | Valid |  | S.7.12 | IDAS OTHERS | Field Equipment Cabinet including switich, APU, I/O Module, etc…and related all component. | 0 | S.7.12 | FR22BE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
191 | Valid |  | S.7.13 | IDAS OTHERS | 1G SFP LC LX SMF transciever for Juniper PE router | 0 | S.7.13 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
192 | Valid |  | S.7.14 | IDAS Camera Pole for MIDS | MIDS Pole 1.2m | 0 | S.7.14 | FF22ZZ00ZZ-0000001 | 1.2 | 0 | 0 | BOTB-PKG2-MR-TE-0001 | SETS | 0
193 | Valid |  | S.7.15 | Steel Structure Support for Field Equipment Cabinet | Steel support 1.2m x 0.8m | 0 | S.7.15 | FF22ZZ00ZZ-0000001 | 1.2 | 0 | 0 | BOTB-PKG2-MR-TE-0001 | SETS | 0
194 | Valid |  | S.7.16 | Security System Intrusion Detection System Main Cabinet | Server and FOPP 42U RACK | 0 | S.7.16 | FR22BA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
195 | Valid |  | S.7.17 | Secrutiy System Optiped for IDAS FOC Connetion | Optiped with Splicing Tray and Kit | 0 | S.7.17 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
196 | Valid |  | S.8 | Security CCTV & ACS System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
197 | Valid |  | S.8.1 | Security ACS Main Cabinet with ACS Controller | 42U ACS/CCTV Enclosure including switch and all related component (ACS Controller, 2 x Reader Interface Module, 2 x Ethernet Switch (POE), 2 x UTP Patch Panel, PSU, PDU, I/O Modules, RS-485 Cable) | 0 | S.8.1 | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 | 1 |  |  | 1
198 | Valid |  | S.8.2 | Security ACS 24 Port Fiber Optic Patch Panel | 24 Port Fiber Optic Patch Panel | 0 | S.8.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 6 | [6 empty] | 2 | 2 |  |  | 2 | [23 empty] | FOC SACS
198 | Valid |  | S.8.3 | Security CCTV & ACS Outdoor CCTV Cabinet - | Field Equipment Cabinets w/ Industrial Ethernet Switch (IES) with Power over Ethernet (POE), (I/O) Module, PSU, FOPP,CB, Tamper Switch | 0 | S.8.3 | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
199 | Valid |  | S.8.4 | Security CCTV Indoor Fixed CCTV Camera - | Indoor Fixed CCTV Camera with Ceilling mount bracket and license | 0 | S.8.4 | FF16ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 24 | [6 empty] | 9 | 6 |  |  | 9
200 | Valid |  | S.8.5 | Security CCTV Fixed CCTV Camera with JB and accessories - | Outdoor Fixed CCTV Camera with wall mount bracket with license | 0 | S.8.5 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 15 | [6 empty] | 6 | 4 |  |  | 5
201 | Valid |  | S.8.6 | Security ACS Proximity Card Reader | Proximity Card Reader | 0 | S.8.6 | FR21AE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 17 | [6 empty] | 5 | 7 |  |  | 5
202 | Valid |  | S.8.7 | Security ACS Electrical Magnetic Lock | Electrical Magnetic Lock | 0 | S.8.7 | FR21AH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 | [6 empty] | 5 | 6 |  |  | 5
203 | Valid |  | S.8.8 | Security ACS Door Contract | Door Contract | 0 | S.8.8 | FR21AI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 36 | [6 empty] | 14 | 8 |  |  | 14
204 | Valid |  | S.8.9 | Security ACS Push Button | Push Button | 0 | S.8.9 | FR21AJ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 15 | [6 empty] | 5 | 5 |  |  | 5
205 | Valid |  | S.8.10 | Security ACS Break Glass Unit | Break Glass Unit | 0 | S.8.10 | FR21AK00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 | [6 empty] | 5 | 6 |  |  | 5
206 | Valid |  | S.8.11 | Security Alarm Siren | Security Alarm Siren |  | S.8.11 | FR21AK00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 8 | [6 empty] | 4 | 0 |  |  | 4
|  |  | S.8.12 | Key Switch-Emergency | Key Switch-Emergency |  | S.8.12 | FR21AK00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 | [6 empty] | 5 | 6 |  |  | 5
207 | Valid |  | S.8.13 | Security CCTV & ACS Surge protector | Enclosure with Cat.6 surge protector | 0 | S.8.13 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
208 | Valid |  | S.8.14 | Tilted pole for Security CCTV | 5m, Hot-dip galvanized steel | 0 | S.8.14 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
209 | Valid |  | S.8.15 | Tilted pole for Security CCTV | 7m, Hot-dip galvanized steel | 0 | S.8.15 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
210 | Valid |  | S.8.16 | CCTV Fixed CCTV Camera with JB and accessories | Explosion Proof |  | S.8.16 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
211 | Valid |  | S.8.17 | CCTV PTZ CCTV Camera with JB and accessories | Explosion Proof |  | S.8.17 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
212 | Valid |  | S.8.18 | Magnetic Sensor (MBS) |  |  | S.8.18 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
213 | Valid |  | S.8.19 | Security ACS Local Enclosure with Controller |  |  | S.8.19 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 24 | [6 empty] | 9 | 6 |  |  | 9 | [23 empty] | Security ACS Local Door Controller (1 Door Capacity)
214 | Valid |  | S.10 | Process CCTV System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
210 | Valid |  | S.10.1 | CCTV Main Cabinet | Main Cabinet | 0 |  | FF11ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
211 | Valid |  | S.10.2 | CCTV Local Cabinet | Local Control Unit with Junction Box | 0 |  | FF12ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
212 | Valid |  | S.10.3 | CCTV Outdoor CCTV Cabinet | Outdoor CCTV Cabinet | 0 |  | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
213 | Valid |  | S.10.4 | CCTV CCTV Workstation with accessories | CCTV Workstation with accessories | 0 |  | FF14ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
214 | Valid |  | S.10.5 | CCTV CCTV Wall Screen Monitor | CCTV Wall Screen Monitor 50" | 0 |  | FF15ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
214 | Valid |  | S.10.6 | CCTV CCTV Wall Screen Monitor | CCTV Wall Screen Monitor 75" | 0 | S.10.5 | FF15ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
215 | Valid |  | S.10.7 | CCTV Indoor Fixed CCTV Camera | Indoor Fixed CCTV Camera | 0 |  | FF16ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
216 | Valid |  | S.10.8 | CCTV Indoor PTZ CCTV Camera | Indoor PTZ CCTV Camera | 0 |  | FF17ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
217 | Valid |  | S.10.9 | CCTV Fixed CCTV Camera with JB and accessories | Weather proof | 0 |  | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
218 | Valid |  | S.10.10 | CCTV Fixed CCTV Camera with JB and accessories | Explosion Proof | 0 |  | FF18ZZ00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
219 | Valid |  | S.10.11 | CCTV PTZ CCTV Camera with JB and accessories | Weather proof | 0 |  | FF19ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
220 | Valid |  | S.10.12 | CCTV PTZ CCTV Camera with JB and accessories | Explosion Proof | 0 |  | FF19ZZ00AD-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
221 | Valid |  | S.10.13 | CCTV CCTV Camera Pole | IDAS Pole up to 3m | 0 |  | FF22ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
222 | Valid |  | S.10.14 | CCTV CCTV Camera Pole | CCTV Camera Pole 3m to 8m Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101V | 0 |  | FF22ZZ00ZZ-0000001 | 5 | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
223 | Valid |  | S.10.15 | CCTV Existing Interface software/license | Existing Interface software/license | 0 |  | FF23ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
224 | Valid |  | S.10.16 | CCTV Server | Server | 0 |  | FF24ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
230 | Valid |  | S.10.16 | Generator Circuit Breaker (GCB) SF6 Type GCB | SF6 Type GCB | 0 |  | FG10ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
231 | Valid |  | S.10.17 | Generator Circuit Breaker (GCB) Vacuum Type GCB | Vacuum Type GCB | 0 |  | FG11ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
227 | Valid |  | S.10.17 | Motion Sensor - Ceiling Type | Ceiling Type | 0 |  | FH00IA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
228 | Valid |  | S.10.18 | Motion Sensor - Wall Mounting Type | Wall Mounting Type | 0 |  | FH00IB00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
229 | Valid |  | S.10.19 | Thermal IR Camera with JB and accessories for Flare stack monitoring | Weather proof | 0 |  | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.10.20 | Composite cable | Between JB to Camera |  | S.10.21 | FF18ZZ00AB-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
230 | Valid |  | S.11 | Process Access Control System | [5 empty] | 0 |  | BOTB-PKG2-MR-TE-0001 |  | 0
231 | Valid |  | S.11.1 | Access Control System Main Cabinet | Main Cabinet | 0 | 91 | FR21AA00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
232 | Valid |  | S.11.2 | Access Control System Local Cabinet | Local Cabinet | 0 | 92 | FR21AB00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
233 | Valid |  | S.11.3 | Access Control System Local Control Unit with Junction Box | Local Control Unit with Junction Box | 0 | 93 | FR21AC00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
234 | Valid |  | S.11.4 | Access Control System ACS Workstation with accessories | ACS Workstation with accessories | 0 | 94 | FR21AD00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
235 | Valid |  | S.11.5 | Access Control System Proximity Card Reader | Proximity Card Reader | 0 | 95 | FR21AE00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
236 | Valid |  | S.11.6 | Access Control System Explosion Proof Card Reader | Explosion Proof Card Reader | 0 | 96 | FR21AF00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
237 | Valid |  | S.11.7 | Access Control System Long Range Card Reader | Long Range Card Reader | 0 | 97 | FR21AG00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
238 | Valid |  | S.11.8 | Access Control System Electrical Magnetic Lock With Door Contact | Electrical Magnetic Lock With Door Contact | 0 | 98 | FR21AH00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
239 | Valid |  | S.11.9 | Access Control System Door Contract | Door Contract | 0 | 99 | FR21AI00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
240 | Valid |  | S.11.10 | Access Control System Push Button | Push Button | 0 | 100 | FR21AJ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
241 | Valid |  | S.11.11 | Access Control System Break Glass Unit | Break Glass Unit | 0 | 101 | FR21AK00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
242 | Valid |  | S.11.12 | Access Control System Turnstiles | Turnstiles | 0 | 102 | FR21AL00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
243 | Valid |  | S.11.13 | Access Control System Speed Gate | Speed Gate | 0 | 103 | FR21AM00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
244 | Valid |  | S.11.14 | Access Control System Vehicle Barrier For Gate | Vehicle Barrier For Gate | 0 | 104 | FR21AN00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
245 | Valid |  | S.11.15 | Access Control System Road Blocker | Road Blocker | 0 | 105 | FR21AO00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
246 | Valid |  | S.11.16 | Access Control System Existing Interface software/license | Existing Interface software/license | 0 | 106 | FR21AP00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
247 | Valid |  | S.11.17 | Access Control System Badge Production System | Badge Production System | 0 | 107 | FR21AQ00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
248 | Valid |  | S.11.18 | Access Control System Alarm Buzzer | Alarm Buzzer | 0 | 108 | FR21AR00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
249 | Valid |  | S.11.19 | Access Control System ACS Pole | ACS Pole up to 3m | 0 | 109 | FR21AS00ZZ-0000001 |  | 0 |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
250 | Valid |  | S.13 | Outside Plant Cable System |  |  | S.13 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
251 | Valid |  | S.13.1 | Fiber Optic Splice Closure | Fire-rated non-buried type |  | S.13.1 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
252 | Valid |  | S.13.2 | 144 core Fiber optic Splice Closure | Branch type (In - one 144 core cable / Out - Three 48 core cable) |  | S.13.2 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
253 | Valid |  | S.13.3 | 48 core Fiber optic Splice Closure | Branch or Butt type (In - one 48 core cable / Out - One 48 core cable) |  | S.13.3 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
254 | Valid |  | S.13.4 | 24 core Fiber optic Splice Closure | Branch or Butt type (In - one 48 core cable / Out - One 48 core cable) |  | S.13.4 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.13.5 | 6 core Fiber optic Splice Closure | Branch or Butt type (In - one 6 core cable / Out - One 6 core cable) | [7 empty] | SETS | 0
255 | Valid |  | S.13.6 | Telecommunication Pedestal | UPC-1278 (IT) |  | S.13.5 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
| Valid |  | S.13.7 | Telecommunication Pedestal | UPC-1278 (NON-IT) |  | S.13.6 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
256 | Valid |  | S.13.8 | Telecommunication Pedestal | UPC-1000 (IT) |  | S.13.7 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
256 | Valid |  | S.13.9 | Telecommunication Pedestal | UPC-1000 (NON-IT) |  | S.13.8 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.10 | Telecommunication Pedestal | OPFOP1420 (IT) |  | S.13.9 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.11 | Telecommunication Pedestal | OPFOP1420 (NON-IT) |  | S.13.10 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.12 | Telecommunication Pedestal | OPFOP1830 |  | S.13.11 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.13 | Telecommunication Pedestal | CAD-8 |  | S.13.12 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.13 | Telecommunication Pedestal | UPC-1278 (SECURITY) |  | S.13.12 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
257 | Valid |  | S.13.14 | Telecommunication Pedestal | OPFOP1420 (SECURITY) |  | S.13.12 |  |  |  |  | BOTB-PKG2-MR-TE-0001 | SETS | 0
Note on F239: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: FSD of PCCTV