## Cover
BOTB (PKG-2) PROJECT
July. 01, 2026
| 기안 | 팀장 | 실장
본 문서의 내용과 관련된 지적재산권에 대한 소유는 현대엔지니어링에 있으며 본문서의 내용에 대한 무단복제 및 무단도용은 법에 저촉됨을 알려 드립니다. Intellectual property right of this document is belongs to Hyundai Engineering. Any reproduction and copy without permission of Hyundai Engineering will be strongly prohibited.

## Cable
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Core/Pair Number | Composition | Conductor Size | Earthing Size | Unit of Cable Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [10 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[18 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | C |  | Cable |  |  |  |  | 0 |  | 0 | 0
2 | Valid |  | C.16 |  | POWER, FLAME RETARDANT, ARMORED |  |  |  |  | 0 |  | 0 | 0
3 | Valid |  |  |  |  | AC POWER CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
4 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
5 | Valid |  |  |  |  | Steel Wired Armored |  |  |  | 0 |  | 0 | 0
6 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
7 | Valid |  |  |  |  | Conductor Color : Black(Live), White(Neutral), Green/Yellow tracer(Ground) |  |  |  | 0 |  | 0 | 0
8 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
9 | Valid |  |  |  |  | Jacket Material and Color : PVC, BLACK |  |  |  | 0 |  | 0 | 0
10 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
11 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
12 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
13 | Valid |  | C.16.1 |  |  |  | 3 x C x 12 AWG | FL, PW, SWA | EC01AC05AK99AF01AA99ZZ99 | 3 | C | 12 | 0 | AWG | M285711381A | M | 7200 | [13 empty] | 3000 | 3000 | [18 empty] | 1200 | for Security, PCCTV Cameras & Industrial Wifi
14 | Valid |  | C.16.1.1 |  |  |  | 3 x C x 12 AWG | TE, PW, SWA |  | 3 | C | 12 | 0 | AWG |  | M | 0
15 | Valid |  | C.16.2 |  |  |  | 3 x C x 10 AWG | FL, PW, SWA | EC01AC05AK99AF01AA99ZZ99 | 3 | C | 10 | 0 | AWG | M367485413A | M | 0
16 | Valid |  | C.16.3 |  |  |  | 3 x C x 2 AWG | TE, PW, SWA |  | 3 | C | 2 | 0 | AWG |  | M | 0
17 | Valid |  | C.16.4 |  |  |  | 3 x C x 6 AWG | TE, PW, SWA |  | 3 | C | 8 | 0 | AWG |  | M | 1600 | [13 empty] | 500 | 500 | [18 empty] | 600 | SACS for Scraper Launcher FEC - 2 x Power Cable
35 | Valid |  | C.17.6 |  |  |  | 2 x C x 14 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 2 | C | 14 | 0 | AWG | M285711331A | M | 400 | [33 empty] | 400 | SACS for Scraper Launcher MSB - Control Cable
18 | Valid |  | C.17 |  | POWER, FLAME RETARDANT, NON-ARMORED |  |  |  |  | 0 |  | 0 | 0
19 | Valid |  |  |  |  | AC POWER CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
20 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
21 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
22 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
23 | Valid |  |  |  |  | Conductor Color : Black(Live), White(Neutral), Green/Yellow tracer(Ground) |  |  |  | 0 |  | 0 | 0
24 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
25 | Valid |  |  |  |  | Jacket Material and Color : PVC, BLACK |  |  |  | 0 |  | 0 | 0
26 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
27 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
28 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
29 | Valid |  | C.17.1 |  |  |  | 3 x C x 14 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 14 | 0 | AWG | M285711330A | M | 0
30 | Valid |  | C.17.2 |  |  |  | 3 x C x 12 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 12 | 0 | AWG | M285711328A | M | 1400 | [16 empty] | 700 | 700 | [16 empty] | SACS for Building - Power Cable
31 | Valid |  | C.17.2.1 |  |  |  | 3 X C X 12 AWG | FL, PW, TE |  | 3 | C | 12 | 0 | AWG |  | M | 0
32 | Valid |  | C.17.3 |  |  |  | 3 x C x 10 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 10 | 0 | AWG | M285711329A | M | 0
33 | Valid |  | C.17.4 |  |  |  | 3 x C x 8 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 8 | 0 | AWG | M414586702A | M | 0
34 | Valid |  | C.17.5 |  |  |  | 3 x C x 6 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 3 | C | 6 | 0 | AWG | M414586703A | M | 4200 | [16 empty] | 600 | 1400 | [8 empty] | 1000 | 200 | 400 | 200 | 200 | 200 |  |  | For Main Cabinet Power, Cube IT
35 | Valid |  | C.17.6 |  |  |  | 2 x C x 14 AWG | FL, PW | EC01AC05AK99AL01AA99ZZ99 | 2 | C | 14 | 0 | AWG | M285711331A | M | 1400 | [16 empty] | 700 | 700 | [16 empty] | SACS for Building - Control Cable
36 | Valid |  | C.18 |  | GROUNDING CABLE |  |  |  |  | 0 |  | 0 | 0
37 | Valid |  |  |  |  | GROUNDING CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
38 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
39 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
40 | Valid |  |  |  |  | PVC insulated |  |  |  | 0 |  | 0 | 0
41 | Valid |  |  |  |  | Jacket Material and Color : EXTRUDED PVC, COLOR GREEN/YELLOW |  |  |  | 0 |  | 0 | 0
42 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
43 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
44 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
45 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
46 | Valid |  | C.18.1 |  |  |  | 1 x C x 10 AWG | FL, GR/YE | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 10 | 0 | AWG | M285711385C | M | 740 | [13 empty] | 270 | 200 |  | 120 | 100 | [15 empty] | 50
[7 empty] | 1 x C x 6 AWG | FL, GR/YE | [7 empty] | M | 1900 | [13 empty] | 1080 | 660 |  | 80 | 80
47 | Valid |  | C.18.2 |  |  |  | 1 x C x 2 AWG | FL, GR/YE | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 2 | 0 | AWG | M285711541C | M | 0
48 | Valid |  | C.18.3 |  |  |  | 1 x C x 2 AWG | FL, GR/YE, TE |  | 1 | C | 2 | 0 | AWG |  | M | 0
49 | Valid |  |  |  |  | GROUNDING CABLE 600/1000V |  |  |  | 0 |  | 0 | 0
50 | Valid |  |  |  |  | FLAME-RETARDANT as per IEC 60332-3-23 (CAT. B) |  |  |  | 0 |  | 0 | 0
51 | Valid |  |  |  |  | Non-Armored |  |  |  | 0 |  | 0 | 0
52 | Valid |  |  |  |  | PVC insulated |  |  |  | 0 |  | 0 | 0
53 | Valid |  |  |  |  | Jacket Material and Color : EXTRUDED PVC, COLOR GREEN |  |  |  | 0 |  | 0 | 0
54 | Valid |  |  |  |  | Conductor Material : Stranded Plain Copper Conductor |  |  |  | 0 |  | 0 | 0
55 | Valid |  |  |  |  | Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
56 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant |  |  |  | 0 |  | 0 | 0
57 | Valid |  |  |  |  | IEC 60502-1 |  |  |  | 0 |  | 0 | 0
58 | Valid |  | C.18.4 |  |  |  | 1 x C x 6 AWG | FL, GR | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 6 | 0 | AWG | M368405088A | M | 0 | [34 empty] | Green insulated #6 AWG copper wire for bonding telecom racks, doors, cable trays, and outdoor devices to TGB/TMGB busbars (SS-072: 70m, PIB-081: 140m, PKG-2 Common: 580m, CCR-1: 40m).
59 | Valid |  | C.18.5 |  |  |  | 1 x C x 6 AWG | FL, GR, TE |  | 1 | C | 6 | 0 | AWG |  | M | 0
60 | Valid |  | C.18.6 |  |  |  | 1 x C x 2 AWG | FL, GR | EC06AC05AK99AL01AA99ZZ99 | 1 | C | 2 | 0 | AWG | M285711541D | M | 0
61 | Valid |  | C.19 |  | FIBER OPTIC, FLAME RETARDANT, AMOURED, OUTDOOR |  |  |  |  | 0 |  | 0 | 0
62 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
63 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, |  |  |  | 0 |  | 0 | 0
64 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
65 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C |  |  |  | 0 |  | 0 | 0
66 | Valid |  |  |  |  | Loose-tybe, Gel-Filled Type (SAES-T-928, 5.8) |  |  |  | 0 |  | 0 | 0
67 | Valid |  |  |  |  | - Wrapping : MICA tape (If Fire resistant) |  |  |  | 0 |  | 0 | 0
68 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar (SAES-T-624, 5.2.4.8) |  |  |  | 0 |  | 0 | 0
69 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Black, minimum 2.35% carbon black concentration, Resistant to Ultra violet light,crude oil, hydrocarbons. |  |  |  | 0 |  | 0 | 0
70 | Valid |  |  |  |  | Sulphur compounds and salt water, Low Smoke Zero Halogen (LSZH) |  |  |  | 0 |  | 0 | 0
71 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
72 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
73 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
74 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
75 | Valid |  |  |  |  | - Fire Resistant to BS6387 Cat. C, W, Z |  |  |  | 0 |  | 0 | 0
76 | Valid |  | C.19.1 |  |  |  | 144 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 144 | C | 0 | 0 |  | M367577766B | M | 8200 | [26 empty] | 8200 | [7 empty] | FOC IT
77 | Valid |  | C.19.2 |  |  |  | 96 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 96 | C | 0 | 0 |  | M367577767B | M | 0
78 | Valid |  | C.19.3 |  |  |  | 72 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 72 | C | 0 | 0 |  | M368405062B | M | 0
79 | Valid |  | C.19.4 |  |  |  | 48 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 48 | C | 0 | 0 |  | M367577765B | M | 8400 | [26 empty] | 8400 | [7 empty] | FOC Non-IT PAS
80 | Valid |  | C.19.5 |  |  |  | 24 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 24 | C | 0 | 0 |  | M367577764B | M | 22450 | [26 empty] | 22450 | [7 empty] | FOC SACS & FOC Non-IT PSA/PMS
81 | Valid |  | C.19.6 |  |  |  | 12 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 12 | C | 0 | 0 |  | M367577768B | M | 11070 |  |  | 8900 | [10 empty] | 570 | 400 | [18 empty] | 1200 | FOC Non IT Analyzer Shelters
82 | Valid |  | C.19.7 |  |  |  | 6 x C | FL, FO, OUTDOOR, TE | EC04ZZ99ZZ03AE07AA99ZZ99 | 4 | C | 0 | 0 |  | M367577763B | M | 14600 |  |  | 9800 | [10 empty] | 1800 | 1800 | [18 empty] | 1200 | FOC PCCTV
83 | Valid |  | C.20 |  | FIBER OPTIC, FIRE RESISTANCE, AMOURED, OUTDOOR |  |  |  |  | 0 |  | 0 | 0
84 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
85 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, |  |  |  | 0 |  | 0 | 0
86 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
87 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C |  |  |  | 0 |  | 0 | 0
88 | Valid |  |  |  |  | Loose-tybe, Gel-Filled Type (SAES-T-928, 5.8) |  |  |  | 0 |  | 0 | 0
89 | Valid |  |  |  |  | - Wrapping : MICA tape (If Fire resistant) |  |  |  | 0 |  | 0 | 0
90 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar (SAES-T-624, 5.2.4.8) |  |  |  | 0 |  | 0 | 0
91 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Black, minimum 2.35% carbon black concentration, Resistant to Ultra violet light,crude oil, hydrocarbons. |  |  |  | 0 |  | 0 | 0
92 | Valid |  |  |  |  | Sulphur compounds and salt water, Low Smoke Zero Halogen (LSZH) |  |  |  | 0 |  | 0 | 0
93 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
94 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
95 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
96 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
97 | Valid |  | C.20.1 |  |  |  | 72 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 72 | C | 0 | 0 |  | M268623721A | M | 0
98 | Valid |  | C.20.2 |  |  |  | 24 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 24 | C | 0 | 0 |  | M268623717A | M | 0
99 | Valid |  | C.20.3 |  |  |  | 12 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 12 | C | 0 | 0 |  | M268623718A | M | 0
100 | Valid |  | C.20.4 |  |  |  | 4 x C | FR FO, OUTDOOR | EC04ZZ99ZZ03AE07AD99ZZ99 | 4 | C | 0 | 0 |  | M268623730A | M | 0
101 | Valid |  | C.21 |  | FIBER OPTIC, FIRE RESISTANCE, AMOURED, INDOOR |  |  |  |  | 0 |  | 0 | 0
102 | Valid |  |  |  |  | <Complied with Cl.4.11 of PP-824554> |  |  |  | 0 |  | 0 | 0
103 | Valid |  |  |  |  | - Reference Standard : ITU-T G-652D, 18-SAMSS-625 (If there are conflict among reference standard, Bidder will follow the most severe requiremet) |  |  |  | 0 |  | 0 | 0
104 | Valid |  |  |  |  | - Mode : Single Mode OS2 (ITU-T G.652D), 9.0/125-micron glass fibre, Zero-Dispersion Low Water Peak, 1310nm wavelength |  |  |  | 0 |  | 0 | 0
105 | Valid |  |  |  |  | - Fiber stand cont : 12 fibres per tube |  |  |  | 0 |  | 0 | 0
106 | Valid |  |  |  |  | - Fiber Stand colour Coding : TIA/EIA 598-C - Housing : Tight Buffer - two(2) layer coating. The first layer shall be a plastic (protective) coating, the second shall be |  |  |  | 0 |  | 0 | 0
107 | Valid |  |  |  |  | acrylate (to repel moisture) |  |  |  | 0 |  | 0 | 0
108 | Valid |  |  |  |  | - Armour Type : All-dielectric (non-metallic), Kevlar |  |  |  | 0 |  | 0 | 0
109 | Valid |  |  |  |  | - Cable Sheath : Polyethylene, Resistant to Ultraviolet light, crude oil, hydrocarbons, Sulphur compounds and salt water, |  |  |  | 0 |  | 0 | 0
110 | Valid |  |  |  |  | Yellow Outer jacket/LSZH-Low Smoke Zero Halogen Outer jacket |  |  |  | 0 |  | 0 | 0
111 | Valid |  |  |  |  | Optical Fiber Non-conductive Plenum (OFNP) type with or without non-metallic moisture barrier |  |  |  | 0 |  | 0 | 0
112 | Valid |  |  |  |  | and shall be listed as being suitable for the purpose, listed as being resistant to spread of fire in accordance with the NEC Article 770 Section 770-26, |  |  |  | 0 |  | 0 | 0
113 | Valid |  |  |  |  | installed in accordance with Section 770-110, and marked in accordance with Table 770-179 |  |  |  | 0 |  | 0 | 0
114 | Valid |  |  |  |  | - Primary coating material : UV curable material |  |  |  | 0 |  | 0 | 0
115 | Valid |  |  |  |  | - Fire rated : NFPA 70 (NEC article 770) |  |  |  | 0 |  | 0 | 0
116 | Valid |  |  |  |  | - Marking / Printing : Metal marking at one-meter intervals describing type, number of cores, manufacturer, year of manufacture |  |  |  | 0 |  | 0 | 0
117 | Valid |  |  |  |  | - Temperature Ragne at operating : -20°C to 70°C |  |  |  | 0 |  | 0 | 0
118 | Valid |  |  |  |  | - Temperature Ragne at storage : -40°C to 70°C |  |  |  | 0 |  | 0 | 0
119 | Valid |  |  |  |  | - All SYSTEM cables shall be "Indoor Fire-resistant cable" type. |  |  |  | 0 |  | 0 | 0
120 | Valid |  | C.21.1 |  |  |  | 24 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 24 | C | 0 | 0 |  | M268623717C | M | 0
121 | Valid |  | C.21.2 |  |  |  | 12 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 12 | C | 0 | 0 |  | M268623718C | M | 0
122 | Valid |  | C.21.3 |  |  |  | 4 x C | FR FO, INDOOR, TE | EC04ZZ99ZZ03AE07AD99ZZ99 | 4 | C | 0 | 0 |  | M268623730C | M | 0
123 | Valid |  | C.22 |  | ETHERNET CABLE |  |  |  |  | 0 |  | 0 | 0
124 | Valid |  |  |  |  | Unsheilded Twisted Pair Cable |  |  |  | 0 |  | 0 | 0
125 | Valid |  |  |  |  | - Separator Material : Flame Retardant Polyolefin |  |  |  | 0 |  | 0 | 0
126 | Valid |  |  |  |  | - Number of Pairs : 4 |  |  |  | 0 |  | 0 | 0
127 | Valid |  |  |  |  | - Cable Pair Color Coding : T568A |  |  |  | 0 |  | 0 | 0
128 | Valid |  |  |  |  | - Conductors : Solid Annealed Copper |  |  |  | 0 |  | 0 | 0
129 | Valid |  |  |  |  | - Conductor Size : 23 AWG |  |  |  | 0 |  | 0 | 0
130 | Valid |  |  |  |  | - Category 6 |  |  |  | 0 |  | 0 | 0
131 | Valid |  |  |  |  | - Reference Specification PP-824554, Section 4.3 |  |  |  | 0 |  | 0 | 0
132 | Valid |  |  |  |  | - UL listed |  |  |  | 0 |  | 0 | 0
133 | Valid |  |  |  |  | - Fire rated : NFPA 70 (NEC article 770) |  |  |  | 0 |  | 0 | 0
134 | Valid |  | C.22.1 |  |  | LS-CMP(Low smoke Plenum) UTP cable | 4 x P x 23AWG | LS-CMP(Low smoke Plenum) UTP, TE | EC04ZZ06AF14AL04ZZ99ZZ99 | 4 | P | 23 | 0 | AWG | M367577797C | M | 3240 | [16 empty] | 1260 | 1980 | [16 empty] | Quantity based on horizontal cable distribution diagrams: 2 runs of 4-pair UTP Category 6A (Plenum CMP grade) per duplex information outlet. MULTIPLY by 90 meters (max length)
135 | Valid |  | C.22.2 |  |  | Gel-Filled UTP Cable (Suitable for Direct Burial and OSP) | 4 x P x 23AWG | Gel-Filled UTP, TE | EC04ZZ06AF14AL04ZZ99ZZ99 | 4 | P | 23 | 0 | AWG | M367577797D | M | 0
136 | Valid |  | C.23 |  | Twisted Pair Cable for Telecommunication System |  |  |  |  | 0 |  | 0 | 0
137 | Valid |  |  |  |  | Twisted Pair, Non Shielded, Armoured, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
138 | Valid |  |  |  |  | Without Overall Shield. |  |  |  | 0 |  | 0 | 0
139 | Valid |  |  |  |  | Steel Wired Armoured |  |  |  | 0 |  | 0 | 0
140 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
141 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
142 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
143 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
144 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant / Gas Blocking |  |  |  | 0 |  | 0 | 0
145 | Valid |  | C.23.1 |  |  |  | 1 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 1 | P | 12 | 0 | AWG | M368405073A | M | 0
146 | Valid |  | C.23.1.1 |  |  |  | 1 x P x 12 AWG | TE, NON ARMROED |  | 1 | P | 12 | 0 | AWG |  | M | 0
147 | Valid |  | C.23.2 |  |  |  | 2 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 2 | P | 12 | 0 | AWG | M368405074A | M | 0
148 | Valid |  | C.23.3 |  |  |  | 6 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 6 | P | 12 | 0 | AWG | M368405075A | M | 0
149 | Valid |  | C.23.4 |  |  |  | 8 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 8 | P | 12 | 0 | AWG | M368405089A | M | 0
150 | Valid |  | C.23.5 |  |  |  | 10 x P x 12 AWG | TE, SWA | EC04AA03AL99AF01BA01ZZ99 | 10 | P | 12 | 0 | AWG | M368405076A | M | 0
151 | Valid |  |  |  |  | Twisted Pair, Shielded, Armoured, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
152 | Valid |  |  |  |  | Overall Shield, Steel Wired Armoured |  |  |  | 0 |  | 0 | 0
153 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
154 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
155 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
156 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
157 | Valid |  |  |  |  | Direct Burial / Oil Resistant / Sun Resistant / Gas Blocking |  |  |  | 0 |  | 0 | 0
158 | Valid |  | C.23.6 |  |  |  | 2 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 2 | P | 16 | 0 | AWG | M368405063A | M | 0
159 | Valid |  | C.23.7 |  |  |  | 4 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 4 | P | 16 | 0 | AWG | M368405064A | M | 0
160 | Valid |  | C.23.8 |  |  |  | 10 x P x 16 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 10 | P | 16 | 0 | AWG | M368405065A | M | 0
161 | Valid |  | C.23.9 |  |  |  | 2 x P x 18 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 2 | P | 18 | 0 | AWG | M368405066A | M | 0
162 | Valid |  | C.23.10 |  |  |  | 4 x P x 18 AWG | TE, SWA | EC04AA03AL99AF01BA01AB99 | 4 | P | 18 | 0 | AWG | M368405067A | M | 0
163 | Valid |  |  |  |  | Twisted Pair, Shielded, Fire Resistant Cable - TC/600V |  |  |  | 0 |  | 0 | 0
164 | Valid |  |  |  |  | Overall Shield |  |  |  | 0 |  | 0 | 0
165 | Valid |  |  |  |  | Primary Insulation Material : Cross Linked Polyethylene(XLPE) insulated |  |  |  | 0 |  | 0 | 0
166 | Valid |  |  |  |  | Conductor Color : BLACK/WHITE |  |  |  | 0 |  | 0 | 0
167 | Valid |  |  |  |  | Conductor Material: Stranded, Circular Copper, per ASTM B3, 7 strands minimum; tinned, per ASTM B33 |  |  |  | 0 |  | 0 | 0
168 | Valid |  |  |  |  | Jacket Material and Color : Fire Resistant BS6387 Cat. C,W,Z , BLACK, Temperature Rating : 90 degC |  |  |  | 0 |  | 0 | 0
169 | Valid |  | C.23.11 |  |  |  | 1 x P x 12 AWG | TE | EC04AA03AL99AL01BA01AB99 | 1 | P | 12 | 0 | AWG | M368405077A | M | 0
170 | Valid |  | C.23.12 |  |  |  | 2 x P x 12 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 12 | 0 | AWG | M368405078A | M | 0
171 | Valid |  | C.23.13 |  |  |  | 2 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 16 | 0 | AWG | M368405079A | M | 0
172 | Valid |  | C.23.14 |  |  |  | 4 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 4 | P | 16 | 0 | AWG | M368405080A | M | 0
173 | Valid |  | C.23.15 |  |  |  | 6 x P x 16 AWG | TE | EC04AA03AL99AL01BA01AB99 | 6 | P | 16 | 0 | AWG | M368405081A | M | 0
174 | Valid |  | C.23.16 |  |  |  | 1 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 1 | P | 18 | 0 | AWG | M368405090A | M | 0
175 | Valid |  | C.23.17 |  |  |  | 2 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 2 | P | 18 | 0 | AWG | M368405082A | M | 0
176 | Valid |  | C.23.18 |  |  |  | 4 x P x 18 AWG | TE | EC04AA03AL99AL01BA01AB99 | 4 | P | 18 | 0 | AWG | M368405083A | M | 0
177 | Valid |  | C.24 |  | Telephone Cable for Telecommunication System |  |  |  |  | 0 |  | 0 | 0
178 | Valid |  |  |  |  | - Jelly Filled |  |  |  | 0 |  | 0 | 0
179 | Valid |  |  |  |  | - Single Shielded (Corrugated Aluminum Tape) |  |  |  | 0 |  | 0 | 0
180 | Valid |  |  |  |  | - Core Wapping Tape |  |  |  | 0 |  | 0 | 0
181 | Valid |  |  |  |  | - LDPE outer sheath |  |  |  | 0 |  | 0 | 0
182 | Valid |  |  |  |  | - Steel Tape Armored. |  |  |  | 0 |  | 0 | 0
183 | Valid |  |  |  |  | - For Underground Installation |  |  |  | 0 |  | 0 | 0
184 | Valid |  |  |  |  | - Fire rated : N/A |  |  |  | 0 |  | 0 | 0
185 | Valid |  | C.24.1 |  |  |  | 100 x P x 22 AWG | TE | EC04ZZ99ZZ99AH99ZZ99ZZ99 | 100 | P | 22 | 0 | AWG | M367577788A | M | 0
186 | Valid |  | C.25 |  | RS-485 Cable |  |  |  |  | 0 |  | 0 | 0
187 | Valid |  | C.25.1 |  |  |  | 4 x P x 18 AWG |  |  | 4 | P | 18 | 0 | AWG |  | M | 0
188 | Valid |  | C.25.2 |  |  |  | 2 x P x 22 AWG |  |  | 2 | P | 22 | 0 | AWG |  | M | 0
189 | Valid |  | C.25.3 |  |  |  | 2 x P x 22 AWG | TE |  | 2 | P | 22 | 0 | AWG |  | M | 0
Note on AF18: HEC: Assumed Location of UPS PDP at field - PCCTV - Industrial Wifi - Flashin Beacon
Note on AG18: HEC: Assumed Location of UPS PDP at field - PCCTV - Industrial Wifi - Flashin Beacon
Note on AZ18: HEC: Assumed Location of UPS PDP at field Security CCTV
Note on AF22: HEC: ESS JB Power from PIB
Note on AG22: HEC: ESS JB Power from PIB
Note on AI36: HEC: Power for the SACS Local Controller
Note on AJ36: HEC: Power for the SACS Local Controller
Note on AI40: HEC: UPS Power SACS Cabinet & PCCTV Cabinet & 1 x UPS Power for Data Network
Note on AJ40: HEC: UPS Power SACS Cabinet & PCCTV Cabinet & IVPS Cabinet & 2 x UPS Power for Data Network & 2 x Emergency Siren System
Note on AS40: HEC: UPS Power SACS Cabinet & PCCTV Cabinet & IVPS Cabinet & 2 x UPS Power for Data Network
Note on AT40: HEC: UPS Power SACS Cabinet
Note on AU40: HEC: 2 x UPS Power for Data Network
Note on AV40: HEC: UPS Power SACS Cabinet
Note on AW40: HEC: UPS Power SACS Cabinet
Note on AX40: HEC: UPS Power for IVPS
Note on AI41: HEC: Control for the SACS Local Controller
Note on AJ41: HEC: Control for the SACS Local Controller
Note on AF52: HEC: Speaker, PCCTV, Flashing Beacon, ESS Siren JB
Note on AG52: HEC: Speaker, PCCTV, Flashing Beacon, ESS Siren JB
Note on AI52: HEC: Speaker, SACS CCTV & PCCTV
Note on AJ52: HEC: Speaker, SACS CCTV & PCCTV
Note on AZ52: HEC: SACS CCTV & MSB
Note on AF53: HEC: Speaker JB & Call Station & Industrial Wifi, Amp. enclosure
Note on AG53: HEC: Speaker JB & Call Station & Industrial Wifi, Amp. enclosure
Note on AI53: HEC: Amp. enclosure
Note on AJ53: HEC: Amp. enclosure
Note on AS84: HEC: IT
Note on AS87: HEC: PAS
Note on AS88: HEC: PSA: 16800 meters SACS: 470 meters PMS: 5180 meters
Note on U89: HEC: Analyzer Shelter
Note on AF89: HEC: Analyzer Shelter
Note on AG89: HEC: Analyzer Shelter
Note on AZ89: HEC: FEC Cabinet to RTU (Assumed Length)
Note on U90: HEC: PCCTV
Note on AF90: HEC: PCCTV to PIB
Note on AG90: HEC: PCCTV to PIB

## Cable Tray
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Cable Tray Width | Cable Tray Height | Thickness | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[16 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | D |  | LADDER CABLE TRAY |  |  |  |  | 0 | 0
2 | Valid |  |  |  | LADDER CABLE TRAY - OUTDOOR | LADDER CABLE TRAY - OUTDOOR |  |  |  | 0 | 0
3 | Valid |  |  |  |  | CABLE TRAY SHALL BE DESIGNED, MANUFACTURED, RATED, TESTED AND MARKED |  |  |  | 0 | 0
4 | Valid |  |  |  |  | IN ACCORDANCE WITH NEMA VE 1 (REFERENCES : SAES-J-902 & SAES-P-104) |  |  |  | 0 | 0
5 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM (MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
6 | Valid |  |  |  |  | - MATERIAL FOR FASTENERS(BOLT, NUT & WASHER & ETC) : 316SS |  |  |  | 0 | 0
7 | Valid |  |  |  |  | - DISTANCE OF CONSECUTIVE RUNGS : 229MM(9") MAXIMUM |  |  |  | 0 | 0
8 | Valid |  |  |  |  | - RUNG LOAD CAPACITY : 90KG MINIMUM |  |  |  | 0 | 0
9 | Valid |  |  |  |  | - ALLOWABLE DEFLECTION : L/100(L=SPAN LENGTH) MAXIMUM |  |  |  | 0 | 0
10 | Valid |  |  |  |  | - VENTILATED TYPE FLANGED COVER : MINIMUM 1.0 MM THICKNESS |  |  |  | 0 | 0
11 | Valid |  |  |  |  | - TRAY THICKNESS : MANUFACTURE STANDARD (MIN. 3.2mm) |  |  |  | 0 | 0
12 | Valid |  |  |  |  | - LOAD / SPAN CLASSS : 20C AS PER NEMA VE1 |  |  |  | 0 | 0
13 | Valid |  |  |  |  | - OUTSIDE FLANGE |  |  |  | 0 | 0
14 | Valid |  |  |  |  | - SPAN : STANDARD SPAN LENGTH 6M |  |  |  | 0 | 0
15 | Valid |  |  |  |  | - FITTINGS RADIUS : 600mm (OUTDOOR) |  |  |  | 0 | 0
16 | Valid |  | D.1 |  | STRAIGHT TRAY | STRAIGHT CABLE TRAY |  |  |  | 0 | 0
17 | Valid |  |  |  |  | - BODY LENGTH : 6.0M |  |  |  | 0 | 0
18 | Valid |  | D.1.1 |  |  | LADDER TRAY STRAIGHT | 152 mm(6") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 150 | 150 | 3.0 | M414586722A | M | 0
19 | Valid |  | D.1.2 |  |  | LADDER TRAY STRAIGHT | 305 mm(12") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 300 | 150 | 3.0 | M414586723A | M | 0
20 | Valid |  | D.1.3 |  |  | LADDER TRAY STRAIGHT | 610 mm(24") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 600 | 150 | 3.0 | M414586724A | M | 0
21 | Valid |  | D.1.4 |  |  | LADDER TRAY STRAIGHT | 915 mm(36") (W) x 152 mm(6") (H) x 3.0 mm(T) | OUTDOOR | ET04AB99AL99ZZ99ZZ | 900 | 150 | 3.0 | M414586725A | M | 43560 |  | 21780 |  |  |  | 21780
22 | Valid |  | D.2 |  | STRAIGHT CABLE TRAY COVER | STRAIGHT CABLE TRAY COVER |  |  |  | 0 | 0
23 | Valid |  |  |  |  | - COVER LENGTH : 3.0M |  |  |  | 0 | 0
24 | Valid |  | D.2.1 |  |  | LADDER TRAY STRAIGHT COVER | 152mm (6") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 150 | 0 | 1 | M349322046A | M | 0
25 | Valid |  | D.2.2 |  |  | LADDER TRAY STRAIGHT COVER | 305 mm(12") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 300 | 0 | 1 | M349322047A | M | 0
26 | Valid |  | D.2.3 |  |  | LADDER TRAY STRAIGHT COVER | 610 mm(24") (W) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 600 | 0 | 1 | M349322048A | M | 0
27 | Valid |  | D.2.4 |  |  | LADDER TRAY STRAIGHT COVER | 915 mm(36") (W)) x 1.0 mm(T) | OUTDOOR | ET02AB99AL99ZZ99ZZ | 900 | 0 | 1 | M349322049A | M | 43560 |  | 21780 |  |  |  | 21780
28 | Valid |  | D.3 |  | HORIZONTAL ELBOW | HORIZONTAL ELBOW (90DEG) WITH COVERS |  |  |  | 0 | 0
29 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
30 | Valid |  | D.3.1 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 150 | 150 | 2.0 | M414586726A | EA | 0
31 | Valid |  | D.3.2 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 300 | 150 | 2.0 | M414586727A | EA | 0
32 | Valid |  | D.3.3 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 600 | 150 | 2.0 | M414586728A | EA | 0
33 | Valid |  | D.3.4 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE03ZZ04ZZ | 900 | 150 | 2.0 | M414586729A | EA | 40 |  | 20 |  |  |  | 20
34 | Valid |  | D.4 |  | HORIZONTAL TEE | HORIZONTAL TEE WITH COVERS |  |  |  | 0 | 0
35 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
36 | Valid |  | D.4.1 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 150 | 150 | 2.0 | M414586730A | EA | 0
37 | Valid |  | D.4.2 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 300 | 150 | 2.0 | M414586731A | EA | 0
38 | Valid |  | D.4.3 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 600 | 150 | 2.0 | M414586732A | EA | 0
39 | Valid |  | D.4.4 |  |  | LADDER TRAY HORIZONTAL TEE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AN03ZZ04ZZ | 900 | 150 | 2.0 | M414586733A | EA | 40 |  | 20 |  |  |  | 20
40 | Valid |  | D.5 |  | HORIZONTAL CROSS | HORIZONTAL CROSS WITH COVERS |  |  |  | 0 | 0
41 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
42 | Valid |  | D.5.1 |  |  | LADDER TRAY HORIZONTAL CROSS WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AA03ZZ99ZZ | 300 | 150 | 2.0 | M414586734A | EA | 0
43 | Valid |  | D.6 |  | VERTICAL ELBOW INSIDE | VERTICAL ELBOW (90DEG) INSIDE WITH COVERS |  |  |  | 0 | 0
44 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
45 | Valid |  | D.6.1 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 150 | 150 | 2.0 | M414586735A | EA | 0
46 | Valid |  | D.6.2 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 300 | 150 | 2.0 | M414586736A | EA | 0
47 | Valid |  | D.6.3 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 600 | 150 | 2.0 | M414586737A | EA | 0
48 | Valid |  | D.6.4 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) INSIDE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE01ZZ04ZZ | 900 | 150 | 2.0 | M414586738A | EA | 40 |  | 20 |  |  |  | 20
49 | Valid |  | D.7 |  | VERTICAL ELBOW OUTSIDE | VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS |  |  |  | 0 | 0
50 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
51 | Valid |  | D.7.1 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 150 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 150 | 150 | 2.0 | M414586739A | EA | 0
52 | Valid |  | D.7.2 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 300 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 300 | 150 | 2.0 | M414586740A | EA | 0
53 | Valid |  | D.7.3 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 600 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 600 | 150 | 2.0 | M414586741A | EA | 0
54 | Valid |  | D.7.4 |  |  | LADDER TRAY VERTICAL ELBOW (90DEG) OUTSIDE WITH COVERS | 900 mm x 150 mm x 2 mm | OUTDOOR | ET04AB99AE02ZZ04ZZ | 900 | 150 | 2.0 | M414586742A | EA | 40 |  | 20 |  |  |  | 20
55 | Valid |  | D.8 |  | REDUCING SPLICE PLATE | REDUCING SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
56 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
57 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
58 | Valid |  | D.8.1 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ99ZZ | 150 | 150 | 2.0 | M414586743A | EA | 0
59 | Valid |  | D.8.2 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 300 mm x 150 mm x 2 mm | OUTDOOR TYPE 1 | ET01AB99ZZ99ZZ99ZZ | 300 | 150 | 2.0 | M414586744A | EA | 0
60 | Valid |  | D.8.3 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 600 mm x 150 mm x 2 mm | OUTDOOR TYPE 2 | ET01AB99ZZ99ZZ99ZZ | 600 | 150 | 2.0 | M414586745A | EA | 0
61 | Valid |  | D.8.4 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 750 mm x 150 mm x 2.6 mm | OUTDOOR TYPE 3 | ET01AB99ZZ99ZZ99ZZ | 750 | 150 | 2.6 | M421387043A | EA | 0
62 | Valid |  | D.9 |  | ADJUSTABLE HORIZONTAL CONNECTOR | ADJUSTABLE HORIZONTAL CONNECTOR |  |  |  | 0 | 0
63 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
64 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
65 | Valid |  | D.9.1 |  |  | LADDER TRAY ADJUSTABLE HORIZONTAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | OUTDOOR TYPE 1 | ET01AB99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M349322058C | EA | 0
66 | Valid |  | D.10 |  | ADJUSTABLE VERTICAL CONNECTOR | ADJUSTABLE VERTICAL CONNECTOR |  |  |  | 0 | 0
67 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
68 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
69 | Valid |  | D.10.1 |  |  | LADDER TRAY ADJUSTABLE VERTICAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | OUTDOOR TYPE 2 | ET01AB99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M349322058D | EA | 0
70 | Valid |  | D.11 |  | BLIND END PLATE | BLIND END PLATE |  |  |  | 0 | 0
71 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
72 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
73 | Valid |  | D.11.1 |  |  | LADDER TRAY BLIND END PLATE | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 150 | 150 | 2.0 | M393921564B | EA | 0
74 | Valid |  | D.11.2 |  |  | LADDER TRAY BLIND END PLATE | 300 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 300 | 150 | 2.0 | M393921565C | EA | 0
75 | Valid |  | D.11.3 |  |  | LADDER TRAY BLIND END PLATE | 600 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 600 | 150 | 2.0 | M393921566B | EA | 0
76 | Valid |  | D.11.4 |  |  | LADDER TRAY BLIND END PLATE | 900 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ07ZZ | 900 | 150 | 2.0 | M393921567B | EA | 40 |  | 20 |  |  |  | 20
77 | Valid |  | D.12 |  | SPLICE PLATE | HEAVY DUTY SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
78 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
79 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
80 | Valid |  | D.12.1 |  |  | LADDER TRAY SPLICE PLATE | 140 mm x 3 mm | OUTDOOR | ET01AB99ZZ99ZZ14ZZ | 0 | 140 | 3.0 | M365749320A | EA | 0
81 | Valid |  | D.13 |  | HEAVY DUTY EXPANSION SPLICE PLATE | HEAVY DUTY EXPANSION SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
82 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
83 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
84 | Valid |  | D.13.1 |  |  | LADDER TRAY HEAVY DUTY EXPANSION SPLICE PLATE | 140 mm x 3 mm | OUTDOOR | ET01AB99ZZ99ZZ08ZZ | 0 | 140 | 3.0 | M414586751A | EA | 0
85 | Valid |  | D.14 |  | GROUND BONDING JUMPER | GROUND BONDING JUMPER |  |  |  | 0 | 0
86 | Valid |  |  |  |  | - MATERIAL : INSULATED COPPER WIRED GROUND CABLE (GREEN &YELLOW TRACER) |  |  |  | 0 | 0
87 | Valid |  |  |  |  | - 35 SQMM x 400 MM LENGTH W/TERMINAL LUG (TINNED COPPER) |  |  |  | 0 | 0
88 | Valid |  |  |  |  | - ACCESSORIES : 316SS SHANK BOLTS & NUTS, WASHER |  |  |  | 0 | 0
89 | Valid |  | D.14.1 |  |  | LADDER TRAY GROUND BONDING JUMPER | None | OUTDOOR | ET01AD99ZZ99ZZ01ZZ | 0 | 0 | 0 | M214244783F | EA | 0 |  | 0 |  |  |  | 0
90 | Valid |  | D.15 |  | HOLD DOWN CLAMP | HOLD DOWN CLAMP |  |  |  | 0 | 0
91 | Valid |  |  |  |  | - MATERIAL : STAINLESS STEEL(316SS) |  |  |  | 0 | 0
92 | Valid |  |  |  |  | - ACCESSORIES : 316SS BOLT & NUT, WASHER |  |  |  | 0 | 0
93 | Valid |  | D.15.1 |  |  | BEAM CLAMP TYPE FOR HORIZONTAL LADDER CABLE TRAY | None | OUTDOOR | ET01AI99ZZ99ZZ19ZZ | 0 | 0 | 0 | M286458936B | EA | 0
94 | Valid |  | D.15.2 |  |  | BEAM GUIDE TYPE FOR HORIZONTAL LADDER CABLE TRAY | None | OUTDOOR TYPE 1 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167M | EA | 0
95 | Valid |  | D.15.3 |  |  | HOLD DOWN BRACKET 2 HOLE (FOR VERTICAL PARTS) | None | OUTDOOR | ET01AI99ZZ99ZZ13ZZ | 0 | 0 | 0 | M349322296B | EA | 0
96 | Valid |  | D.15.4 |  |  | HOLD DOWN CLAMP WITH SPRING NUT (For U-Channel) | None | OUTDOOR TYPE 2 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167N | EA | 0
97 | Valid |  | D.15.5 |  |  | GUIDE TYPE CLAMP WITH SPRING NUT (For U-Channel) | None | OUTDOOR TYPE 3 | ET01AI99ZZ99ZZ99ZZ | 0 | 0 |  | M272892167O | EA | 0
98 | Valid |  | D.15.6 |  |  | HOLD DOWN BRACKET 4 HOLE (FOR VERTICAL PARTS) | None | OUTDOOR | ET01AI99ZZ99ZZ99ZZ | 0 | 0 | 0 | M272892167B | EA | 0 |  | 0 |  |  |  | 0
99 | Valid |  | D.16 |  | HEAVY DUTY CABLE TRAY COVER CLAMP | HEAVY DUTY CABLE TRAY COVER CLAMP |  |  |  | 0 | 0
100 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
101 | Valid |  |  |  |  | - COMPLETE WITH BOLT & NUTS & WWASHER : 316SS |  |  |  | 0 | 0
102 | Valid |  |  |  |  | - COMPLETE WITH NON-METALIC WASHER(GASKET) SUCH AS TEFLON OR NITRILE RUBBER TO WITHSTAND CORROSION |  |  |  | 0 | 0
103 | Valid |  | D.16.1 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 150 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 150 | 150 | 2.0 | M414586746A | EA | 0
104 | Valid |  | D.16.2 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 300 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 300 | 150 | 2.0 | M414586747A | EA | 0
105 | Valid |  | D.16.3 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 600 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 600 | 150 | 2.0 | M414586748A | EA | 0
106 | Valid |  | D.16.4 |  |  | HEAVY DUTY CABLE TRAY COVER CLAMP | 900 mm x 150 mm x 2 mm | OUTDOOR | ET01AB99ZZ99ZZ03ZZ | 900 | 150 | 2.0 | M414586749A | EA | 0 |  | 0 |  |  |  | 0
107 | Valid |  |  |  | LADDER CABLE TRAY - INDOOR | LADDER CABLE TRAY - INDOOR |  |  |  | 0 | 0
108 | Valid |  |  |  |  | CABLE TRAY SHALL BE DESIGNED, MANUFACTURED, RATED, TESTED AND MARKED |  |  |  | 0 | 0
109 | Valid |  |  |  |  | IN ACCORDANCE WITH NEMA VE 1 (REFERENCES : SAES-J-902 & SAES-P-104) |  |  |  | 0 | 0
110 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM (MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
111 | Valid |  |  |  |  | - MATERIAL FOR FASTENERS(BOLT, NUT & WASHER & ETC) : 316SS |  |  |  | 0 | 0
112 | Valid |  |  |  |  | - DISTANCE OF CONSECUTIVE RUNGS : 229MM(9") MAXIMUM |  |  |  | 0 | 0
113 | Valid |  |  |  |  | - RUNG LOAD CAPACITY : 90KG MINIMUM |  |  |  | 0 | 0
114 | Valid |  |  |  |  | - ALLOWABLE DEFLECTION : L/100(L=SPAN LENGTH) MAXIMUM |  |  |  | 0 | 0
115 | Valid |  |  |  |  | - TRAY THICKNESS : MANUFACTURE STANDARD (MIN. 3.2mm) |  |  |  | 0 | 0
116 | Valid |  |  |  |  | - LOAD / SPAN CLASSS : 20C AS PER NEMA VE1 |  |  |  | 0 | 0
117 | Valid |  |  |  |  | - OUTSIDE FLANGE |  |  |  | 0 | 0
118 | Valid |  |  |  |  | - SPAN : STANDARD SPAN LENGTH 6M |  |  |  | 0 | 0
119 | Valid |  |  |  |  | - FITTINGS RADIUS : 300mm (INDOOR) |  |  |  | 0 | 0
120 | Valid |  | D.17 |  | STRAIGHT TRAY | STRAIGHT CABLE TRAY |  |  |  | 0 | 0
121 | Valid |  |  |  |  | - BODY LENGTH : 6.0M |  |  |  | 0 | 0
122 | Valid |  | D.17.1 |  |  | LADDER TRAY STRAIGHT | 152 mm(6") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 150 | 150 | 3.0 | M414586722B | M | 600 | [16 empty] | 240 | 360 | [16 empty] | SACS UPS & Controller
123 | Valid |  | D.17.2 |  |  | LADDER TRAY STRAIGHT | 305 mm(12") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 300 | 150 | 3.0 | M414586723B | M | 161.1 | [16 empty] | 57 | 104.1
124 | Valid |  | D.17.3 |  |  | LADDER TRAY STRAIGHT | 457 mm(18") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 450 | 150 | 3.0 | M414586750A | M | 0
125 | Valid |  | D.17.4 |  |  | LADDER TRAY STRAIGHT | 610 mm(24") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 600 | 150 | 3.0 | M414586724B | M | 50 | [7 empty] | 50
126 | Valid |  | D.17.5 |  |  | LADDER TRAY STRAIGHT | 915 mm(36") (W) x 152 mm(6") (H) x 3.0 mm(T) | INDOOR | ET04AB99AL99ZZ99ZZ | 900 | 150 | 3.0 | M414586725B | M | 0
127 | Valid |  | D.18 |  | HORIZONTAL ELBOW | HORIZONTAL ELBOW (90DEG) WITHOUT COVERS |  |  |  | 0 | 0
128 | Valid |  |  |  |  | - RADIUS : 600mm |  |  |  | 0 | 0
129 | Valid |  | D.18.1 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 150 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 150 | 150 | 2.0 | M414586726B | EA | 0
130 | Valid |  | D.18.2 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 300 | 150 | 2.0 | M414586727B | EA | 10 | [16 empty] | 5 | 5
131 | Valid |  | D.18.3 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 600 | 150 | 2.0 | M414586728B | EA | 5 | [7 empty] | 5
132 | Valid |  | D.18.4 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 900 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 900 | 150 | 2.0 | M414586729B | EA | 0
133 | Valid |  | D.18.5 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 450 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ04ZZ | 450 | 150 | 2 | M421387044A | EA | 0
134 | Valid |  |  |  |  | - RADIUS : 300mm |  |  |  | 0 | 0
135 | Valid |  | D.18.6 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ02ZZ | 300 | 150 | 2 | M421387045A | EA | 10 | [16 empty] | 5 | 5
136 | Valid |  | D.18.7 |  |  | LADDER TRAY HORIZONTAL ELBOW (90DEG) WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AE03ZZ02ZZ | 600 | 150 | 2 | M421387046A | EA | 5 | [7 empty] | 5
137 | Valid |  | D.19 |  | HORIZONTAL TEE | HORIZONTAL TEE WITHOUT COVERS |  |  |  | 0 | 0
138 | Valid |  |  |  |  | - RADIUS : 300mm |  |  |  | 0 | 0
139 | Valid |  | D.19.1 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 300 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 300 | 150 | 2.0 | M414586731B | EA | 10 | [16 empty] | 5 | 5
140 | Valid |  | D.19.2 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 600 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 600 | 150 | 2.0 | M414586732B | EA | 5 | [7 empty] | 5
141 | Valid |  | D.19.3 |  |  | LADDER TRAY HORIZONTAL TEE WITHOUT COVERS | 900 mm x 150 mm x 2 mm | INDOOR | ET04AB99AN03ZZ04ZZ | 900 | 150 | 2.0 | M414586733B | EA | 0
142 | Valid |  | D.20 |  | REDUCING SPLICE PLATE | REDUCING SPLICE PLATE (HEIGHT 140) |  |  |  | 0 | 0
143 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINUM (MAX. 0.4% COPPER) |  |  |  | 0 | 0
144 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
145 | Valid |  | D.20.1 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 600 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 600 | 150 | 2.0 | M414586745B | EA | 5 | [7 empty] | 5
146 | Valid |  | D.20.2 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 300 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 300 | 150 | 2 | M414586744B | EA | 10 | [16 empty] | 5 | 5
147 | Valid |  | D.20.3 |  |  | LADDER TRAY REDUCING SPLICE PLATE | 450 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ99ZZ | 450 | 150 | 2 | M421387047A | EA | 0
148 | Valid |  | D.21 |  | ADJUSTABLE HORIZONTAL CONNECTOR | ADJUSTABLE HORIZONTAL CONNECTOR |  |  |  | 0 | 0
149 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
150 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
151 | Valid |  | D.21.1 |  |  | ADJUSTABLE HORIZONTAL CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | INDOOR | ET01AI99ZZ99ZZ11ZZ | 0 | 150 | 3.0 | M367485430A | EA | 0
152 | Valid |  | D.22 |  | ADJUSTABLE VERTICAL CONNECTOR | ADJUSTABLE VERTICAL RISER CONNECTOR |  |  |  | 0 | 0
153 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
154 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
155 | Valid |  | D.22.1 |  |  | ADJUSTABLE VERTICAL RISER CONNECTOR (2 PIECE / EA) | 150 mm x 3 mm | INDOOR | ET01AI99ZZ99ZZ12ZZ | 0 | 150 | 3.0 | M367485431A | EA | 0
156 | Valid |  | D.23 |  | BLIND END PLATE | BLIND END PLATE |  |  |  | 0 | 0
157 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
158 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
159 | Valid |  | D.23.1 |  |  | LADDER TRAY BLIND END PLATE | 300 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 300 | 150 | 2.0 | M393921565D | EA | 10 | [16 empty] | 5 | 5
160 | Valid |  | D.23.2 |  |  | LADDER TRAY BLIND END PLATE | 600 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 600 | 150 | 2.0 | M393921566C | EA | 5 | [7 empty] | 5
161 | Valid |  | D.23.3 |  |  | LADDER TRAY BLIND END PLATE | 900 mm x 150 mm x 2 mm | INDOOR | ET01AB99ZZ99ZZ07ZZ | 900 | 150 | 2.0 | M393921567C | EA | 0
162 | Valid |  | D.24 |  | SPLICE PLATE | SPLICE PLATE |  |  |  | 0 | 0
163 | Valid |  |  |  |  | - MATERIAL : COPPER-FREE ALUMINIUM(MAXIMUM OF 0.4% COPPER) |  |  |  | 0 | 0
164 | Valid |  |  |  |  | - ACCESSORIES : BOLT & NUT (316SS) |  |  |  | 0 | 0
165 | Valid |  | D.24.1 |  |  | SPLICE PLATE | 140 mm x 3 mm | INDOOR | ET01AB99ZZ99ZZ14ZZ | 0 | 140 | 3.0 | M365749320B | EA | 0
166 | Valid |  | D.25 |  | GROUND BONDING JUMPER | GROUND BONDING JUMPER |  |  |  | 0 | 0
167 | Valid |  |  |  |  | - MATERIAL : INSULATED COPPER WIRED GROUND CABLE (GREEN &YELLOW TRACER) |  |  |  | 0 | 0
168 | Valid |  |  |  |  | - 35 SQMM x 400 MM LENGTH W/TERMINAL LUG |  |  |  | 0 | 0
169 | Valid |  |  |  |  | - ACCESSORIES : 316SS SHANK BOLTS & NUTS, WASHER |  |  |  | 0 | 0
170 | Valid |  | D.25.1 |  |  | GROUND BONDING JUMPER | None | INDOOR | ET01AD99ZZ99ZZ01ZZ | 0 | 0 | 0 | M214244783G | EA | 0 | [16 empty] | 0 | 0
171 | Valid |  | D.26 |  | HOLD DOWN CLAMP | HOLD DOWN CLAMP |  |  |  | 0 | 0
172 | Valid |  |  |  |  | - MATERIAL : 316SS |  |  |  | 0 | 0
173 | Valid |  |  |  |  | - ACCESSORIES : 316SS BOLT & NUT, WASHER |  |  |  | 0 | 0
174 | Valid |  | D.26.1 |  |  | HOLD DOWN CLAMP | None | INDOOR | ET01AI99ZZ99ZZ10ZZ | 0 | 0 |  | M286458938N | EA | 0 | [16 empty] | 0 | 0
175 | Valid |  |  |  |  | 177667 |  |  |  | 0 | 0
176 | Valid |  |  |  |  | 149709 |  |  |  | 0 | 0
Note on R26: HEC: 150m 6500m OSP Security 5800m OSP PAS 5700m OSP PSA
Note on R32: HEC: 150m 6500m OSP Security 5800m OSP PAS 5700m OSP PSA

## Conduit
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Conduit Size | Unit of Conduit Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [7 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[15 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | G |  | CONDUIT
2 | Valid |  | G.1 |  | RIGID STEEL GALVANIZED CONDUIT (RSGC)
3 | Valid |  |  |  |  | - ANSI C80.1 RIGID GALVANIZED STEEL WITH PVC COATED
4 | Valid |  |  |  |  | (MIN. TKS OF PVC : 40 MILS (1MM) PER NEMA RN1.)
5 | Valid |  |  |  |  | - BOTH ENDS NPT THREADED WITH COUPLING SCREWED ON ONE ENDS.
6 | Valid |  | G.1.1 |  |  | LENGTH : 3M | 1" | For Instrument | EU04AI02AC07 | 1 | inch | M220652764C | M | 0
7 | Valid |  | G.1.2 |  |  | LENGTH : 3M | 1-1/4" | For Instrument | EU04AI02AC07 | 1.25 | inch | M220652765A | M | 0
8 | Valid |  | G.1.3 |  |  | LENGTH : 3M | 1-1/2" | For Instrument | EU04AI02AC07 | 1.5 | inch | M220652766B | M | 0
9 | Valid |  | G.1.4 |  |  | LENGTH : 3M | 2" | For Instrument | EU04AI02AC07 | 2 | inch | M220652767B | M | 0
10 | Valid |  | G.1.5 |  |  | LENGTH : 3M | 4" | For Instrument | EU04AI02AC07 | 4 | inch | M347616303A | M | 0
11 | Valid |  | G.1.6 |  |  | LENGTH : 3M | 3/4" | For Telecom | EU04AI02AC07 | 0.75 | inch | M220652763A | M | 0
12 | Valid |  | G.1.7 |  |  | LENGTH : 3M | 1" | For Telecom | EU04AI02AC07 | 1 | inch | M220652764B | M | 600 |  | 300 |  |  |  | 300 | [28 empty] | for branching out from main tray
13 | Valid |  | G.1.8 |  |  | LENGTH : 3M | 1-1/2" | For Telecom | EU04AI02AC07 | 1.5 | inch | M220652766A | M | 0
14 | Valid |  | G.1.9 |  |  | LENGTH : 3M | 2-1/2" | For Telecom | EU04AI02AC07 | 2.5 | inch | M414586752A | M | 0
15 | Valid |  | G.1.10 |  |  | LENGTH : 3M | 1-1/4" | For Telecom | EU04AI02AC07 | 1.25 | inch | M220652765B | M | 0
16 | Valid |  | G.1.12 |  |  | LENGTH : 3M | 4" | For Telecom | EU04AI02AC07 | 4 | inch | M347616303B | M | 0
17 | Valid |  | G.2 |  | PVC PIPE CONDUIT
18 | Valid |  |  |  |  | - DB-120 As per NEMA TC 6 & 8
19 | Valid |  |  |  |  | - Colored Gray, With One Coupling
20 | Valid |  | G.2.1 |  |  | LENGTH : 6M | 1" | For Telecom | EU03AB99ZZ99 | 1 | inch | M191110753D | M | 4000 |  | 2000 |  |  |  | 2000 | [28 empty] | outdoor lateral runs connecting outdoor cameras, paging intercoms , and outdoor WAP enclosures to nearest routing points
21 | Valid |  | G.2.2 |  |  | LENGTH : 6M | 1-1/4" | For Telecom | EU03AB99ZZ99 | 1.25 | inch | M220652663B | M | 0
22 | Valid |  | G.2.3 |  |  | LENGTH : 6M | 2" | For Telecom | EU03AB99ZZ99 | 2 | inch | M190965498H | M | 0
23 | Valid |  | G.2.4 |  |  | LENGTH : 6M | 4" | For Telecom | EU03AB99ZZ99 | 4 | inch | M190965501F | M | 0
24 | Valid |  | G.2.5 |  |  | LENGTH : 6M | 6" | For Instrument | EU03AB99ZZ99 | 6 | inch | M347616320D | M | 0
25 | Valid |  | G.2.5.1 |  |  | LENGTH : 6M | 1-1/2" | For Telecom | EU03AB99ZZ99 | 1.5 | inch | M190965497A | M | 0
26 | Valid |  | G.2.5.2 |  |  | LENGTH : 6M | 4" | For Instrument | EU03AB99ZZ99 | 4 | inch | M190965501I | M | 0
27 | Valid |  |  |  |  | - TYPE EB-20, NEMA TC 6 & 8
28 | Valid |  |  |  |  | - Colored Gray, Without Coupling
29 | Valid |  | G.2.6 |  |  | LENGTH : 3M | 2" | FOR WALL OPENING | EU03AB99ZZ99 | 2 | inch | M190965498G | M | 0
30 | Valid |  | G.2.7 |  |  | LENGTH : 3M | 3" | FOR WALL OPENING | EU03AB99ZZ99 | 3 | inch | M190965500D | M | 0
31 | Valid |  | G.2.8 |  |  | LENGTH : 3M | 1" | FOR WALL OPENING | EU03AB99ZZ99 | 1 | inch | M191110753E | M | 0
32 | Valid |  | G.3 |  | EMT CONDUIT
33 | Valid |  |  |  |  | - ANSI C80.3, UL797
34 | Valid |  |  |  |  | - WITH ONE END COUPLING
35 | Valid |  | G.3.1 |  |  | LENGTH : 6M | 1" | For Telecom | EU04AM05AB99 | 1 | inch | M367575811B | M | 750 | [16 empty] | 215 | 535 | [16 empty] | IVPS, SCS
36 | Valid |  | G.3.2 |  |  | LENGTH : 6M | 1-1/4" | For Telecom | EU04AM05AB99 | 1.25 | inch | M367575812B | M | 0
37 | Valid |  | G.3.3 |  |  | LENGTH : 6M | 1-1/2" | For Telecom | EU04AM05AB99 | 1.5 | inch | M368407344A | M | 0
38 | Valid |  | G.3.4 |  |  | LENGTH : 6M | 2" | For Telecom | EU04AM05AB99 | 2 | inch | M368407345A | M | 20 | [16 empty] | 20 | [17 empty] | for PSA
39 | Valid |  | G.3.5 |  |  | LENGTH : 6M | 2-1/2" | For Telecom | EU04AM05AB99 | 2.5 | inch | M390258549A | M | 0
40 | Valid |  | G.3.6 |  |  | LENGTH : 6M | 1/2" | For Telecom | EU04AM05AB99 | 0.5 | inch | M414586753A | M | 0
41 | Valid |  | G.3.7 |  |  | LENGTH : 6M | 3/4" | For Telecom | EU04AM05AB99 | 0.75 | inch | M414586754A | M | 0
42 | Valid |  | G.4 |  | Corrugated Optical Duct (C.O.D)
43 | Valid |  |  |  |  | - HDPE corrugated pipe with 110mm (4") outer diameter, orange color
44 | Valid |  | G.4.1 |  |  | C.O.D with 5-1" Sub-ducts with pulling rope, 5 sub-duct color code : Blue/Orange/Green/White/Black | 4" | C.O.D with 5-1" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826A | M | 0
45 | Valid |  | G.4.2 |  |  | C.O.D with 4-1" Sub-ducts with pulling rope, 4 sub-duct color code : Blue/Orange/Green/White | 4" | C.O.D with 4-1" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826B | M | 600 | [13 empty] | 300 | 300 | [19 empty] | FO CCTV
46 | Valid |  | G.4.3 |  |  | C.O.D with 3-1 1/2" Sub-ducts with pulling rope, 3 sub-duct color code : Orange/Green/White | 4" | C.O.D with 3-1 1/2" Sub-ducts | EU02AG05AB99 | 4 | inch | M367575826C | M | 0
47 | Valid |  | G.4.4 |  |  | C.O.D without Sub-duct | 4" | C.O.D without Sub-duct | EU02AG05AB99 | 4 | inch | M367575826D | M | 0
48 | Valid |  | G.4.5 |  |  | C.O.D without Sub-duct | 150 mm | C.O.D without Sub-duct | EU02AG05AB99 | 150 | mm | M414586757A | M | 0
49 | Valid |  | G.5 |  | Flexible Conduit
50 | Valid |  |  |  |  | - UL LIQUIDTIGHT FLEXIBLE METAL CONDUIT (FOR CLASS 1, ZONE 2) WITH PVC COATED
51 | Valid |  |  |  |  | - TEMPERATURE RATING ≥ 80℃
52 | Valid |  | G.5.1 |  |  |  | 1" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 1 | inch | M368429397D | M | 0
53 | Valid |  | G.5.2 |  |  |  | 1-1/2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 1.5 | inch | M368429398D | M | 0
54 | Valid |  | G.5.3 |  |  |  | 2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 2 | inch | M368429399B | M | 0
55 | Valid |  | G.5.4 |  |  |  | 2-1/2" | NPT(M) x NPT(F) (for Instrument) | EU02AE02ZZ07 | 2.5 | inch | M368429400C | M | 0
56 | Valid |  | G.5.5 |  |  |  | 1" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1 | inch | M368429397B | M | 0
57 | Valid |  | G.5.6 |  |  |  | 3/4" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | .75 | inch | M390284338A | EA | 0
58 | Valid |  | G.5.7 |  |  |  | 1/2" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 0.5 | inch | M421387002A | M | 0
59 | Valid |  | G.5.8 |  |  |  | 1-1/4" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1.25 | inch | M421387003A | M | 0
60 | Valid |  | G.5.9 |  |  |  | 1-1/2" | NPT(M) x NPT(F) (for Telecom) | EU02AE02ZZ07 | 1.5 | inch | M368429398E | M | 0
61 | Valid |  | G.6 |  | FLEXIBLE METALLIC CONDUIT
62 | Valid |  |  |  |  | UL listed, Gavanized Steel Type FMC
63 | Valid |  | G.6.1 |  |  |  | 3/4" | 3/4'', for Telecom | EU02AE02ZZ07 | 0.75 | inch | M390284338B | M | 0
64 | Valid |  | G.6.2 |  |  |  | 1" | 1", for Telecom | EU02AE02ZZ07 | 1 | inch | M368429397C | M | 0
65 | Valid |  | G.6.3 |  |  |  | 1-1/2" | 1-1/2", for Telecom | EU02AE02ZZ07 | 1.5 | inch | M368429398B | M | 0
66 | Valid |  | G.7 |  | HDPE Sub-duct
67 | Valid |  |  |  |  | UL listed, Gavanized Steel Type FMC
68 | Valid |  | G.7.1 |  | HDPE Sub-duct |  | 1" | Green, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016A | M | 6000 |  | 3000 |  |  |  | 3000
69 | Valid |  | G.7.2 |  | HDPE Sub-duct |  | 1" | Blue, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016B | M | 6000 |  | 3000 |  |  |  | 3000
70 | Valid |  | G.7.3 |  | HDPE Sub-duct |  | 1" | White, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016C | M | 6000 |  | 3000 |  |  |  | 3000
71 | Valid |  | G.7.4 |  | HDPE Sub-duct |  | 1" | Orange, for Telecom | EU02AG02ZZ99 | 1 | inch | M421387016D | M | 6000 |  | 3000 |  |  |  | 3000
Note on AF40: HEC: IVPS=170meters SCS=45meters
Note on AG40: HEC: IVPS=180meters SCS=355meters
Note on AC50: HEC: FO PCCTV
Note on AD50: HEC: FO PCCTV
Note on Q73: HEC: IT:9000 Non-IT:2000 Security:1000
Note on Q74: HEC: IT:9000 Non-IT:2000 Security:1000
Note on Q75: HEC: IT:9000 Non-IT:2000 Security:1000
Note on Q76: HEC: IT:9000 Non-IT:2000 Security:1000

## Cable Gland
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Gland Size | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [6 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[14 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | I |  | CABLE GLAND
2 | Valid |  | I.1 |  | ARMORED CABLE GLAND
3 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
4 | Valid |  |  |  |  | - Seal ring and compound barrier seal
5 | Valid |  |  |  |  | - Sealing ring kit, PCV shroud, Locknut, Earth Tag, Washer
6 | Valid |  |  |  |  | - Material including metal fastener : 316SS
7 | Valid |  |  |  |  | - Shall be designed to bond the armor ( listed as suitable for grounding )
8 | Valid |  |  |  |  | and bond the armored to the gland
9 | Valid |  | I.1.1 |  |  |  | M20 | M20.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318D | EA | 0
10 | Valid |  | I.1.2 |  |  |  | M25 | M25.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 25 | M388017319C | EA | 0
11 | Valid |  | I.1.3 |  |  |  | M32 | M32.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 32 | M388017320C | EA | 0
12 | Valid |  | I.1.4 |  |  |  | M40 | M40.M, SEALING RANGE : 3 | ED01AI99AE01ZZ10AD99ZZ | 40 | M388017321C | EA | 0
13 | Valid |  | I.1.5 |  |  |  | M20 | M20.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318C | EA | 0 | [34 empty] | Armored M20 cable glands for outdoor telecom and security devices. Sourced from PTZ: 48, FEC: 6, IAP: 27, OSP: 20, and IVPS: 228. Quantities: SS-070: 3, SS-071: 3, PKG-2 Common: 323.
14 | Valid |  | I.1.6 |  |  |  | M25 | M25.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 25 | M388017319B | EA | 1995 |  |  | 1285 |  |  |  | 80 | 75 | [5 empty] | 225 | 150 |  | 70 | 60 | [15 empty] | 50 | Armored M25 cable glands for outdoor telecom, security, and power devices. Includes 121 telecom glands + 28 power cable glands (field ends).
15 | Valid |  | I.1.7 |  |  |  | M32 | M32.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 32 | M388017320B | EA | 0 | [34 empty] | Armored M32 cable glands for outdoor telecom and security devices. Sourced from FEC: 3 and OSP: 15. Quantities: PKG-2 Common: 18.
16 | Valid |  | I.1.8 |  |  |  | M40 | M40.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 40 | M388017321B | EA | 0
17 | Valid |  | I.1.9 |  |  |  | M50 | M50.M, FOR TELECOM | ED01AI99AE01ZZ10AD99ZZ | 50 | M421387008A | EA | 0
18 | Valid |  | I.1.10 |  |  |  | M20 | M20.M, SEALING RANGE : 2 | ED01AI99AE01ZZ10AD99ZZ | 20 | M388017318E | EA | 0
19 | Valid |  | I.2 |  | NON-ARMORED CABLE GLAND
20 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
21 | Valid |  |  |  |  | - Seal ring and compound barrier seal
22 | Valid |  |  |  |  | - Sealing ring kit, PCV shroud, Locknut, Earth Tag, Washer
23 | Valid |  |  |  |  | - Material including metal fastener : 316SS
24 | Valid |  |  |  |  | - METRIC.M X METRIC.F for Flexible Conduit Connection
25 | Valid |  | I.2.1 |  |  |  | M20 | M20.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322E | EA | 0
26 | Valid |  | I.2.2 |  |  |  | M25 | M25.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323F | EA | 0
27 | Valid |  | I.2.3 |  |  |  | M32 | M32.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324G | EA | 0
28 | Valid |  | I.2.4 |  |  |  | M40 | M40.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325G | EA | 0
29 | Valid |  | I.2.5 |  |  |  | M50 | M50.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326F | EA | 0
30 | Valid |  | I.2.6 |  |  |  | M63 | M63.M, NON-ARMORED, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333D | EA | 0
31 | Valid |  | I.2.7 |  |  |  | M40 | M40.M X M40.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325H | EA | 0
32 | Valid |  | I.2.8 |  |  |  | M50 | M50.M X M50.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326G | EA | 0
33 | Valid |  | I.2.9 |  |  |  | M63 | M63.M X M63.F, SEALING RANGE : 2, | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333E | EA | 0
34 | Valid |  | I.2.10 |  |  |  | 1/2" | 1/2"NPT.M X M20.F, SEALING RANGE : 3 | ED03AI99AE01ZZ10AD99ZZ | .5 | M421387011A | EA | 0
35 | Valid |  | I.2.11 |  |  |  | 3/4" | 3/4"NPT.M X M25.F, SEALING RANGE : 2 | ED03AI99AE01ZZ10AD99ZZ | 0.75 | M421387013A | EA | 0
36 | Valid |  | I.2.12 |  |  |  | M20 | M20.M, NON-ARMORED, FOR TELECOM | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322F | EA | 52 | [6 empty] | 8 | 8 | [8 empty] | 20 | 16 | [16 empty] | Non-armored M20 cable glands for outdoor fixed cameras. Quantities updated based on camera counts (2 glands per camera): SS-070: 8, PIB-080: 8, SS-071: 8, SS-072: 20, PIB-081: 16.
37 | Valid |  | I.2.13 |  |  |  | M25 | M25.M, NON-ARMORED, FOR TELECOM | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323G | EA | 52 | [6 empty] | 8 | 8 | [8 empty] | 20 | 16 | [16 empty] | Assumed
38 | Valid |  | I.3 |  | ADAPTOR
39 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
40 | Valid |  |  |  |  | - 316SS, METRIC threaded, 'O' Ring (Male x Female)
41 | Valid |  | I.3.1 |  |  |  | M25 | M20. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323B | EA | 0
42 | Valid |  | I.3.2 |  |  |  | M32 | M20. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324B | EA | 0
43 | Valid |  | I.3.3 |  |  |  | M32 | M25. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324C | EA | 0
44 | Valid |  | I.3.4 |  |  |  | M40 | M25. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325B | EA | 0
45 | Valid |  | I.3.5 |  |  |  | M40 | M32. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325C | EA | 0
46 | Valid |  | I.3.6 |  |  |  | M50 | M32. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326B | EA | 0
47 | Valid |  | I.3.7 |  |  |  | M50 | M40. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326C | EA | 0
48 | Valid |  | I.3.8 |  |  |  | M63 | M40. M x M63. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333A | EA | 0
49 | Valid |  | I.3.9 |  |  |  | M63 | M50. M x M63. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333B | EA | 0
50 | Valid |  | I.3.9.1 |  |  |  | 1/2" | 1/2"NPT(M) x M20(F) | ED03AI99AE01ZZ10AD99ZZ | .5 | M421387011B | EA | 0
51 | Valid |  | I.3.9.2 |  |  |  | 3/4" | 3/4"NPT(M) x M25(F) | ED03AI99AE01ZZ10AD99ZZ | .75 | M421387013B | EA | 0
52 | Valid |  | I.3.9.3 |  |  |  | 1" | 1"NPT(M) x M32(F) | ED03AI99AE01ZZ10AD99ZZ | 1 | M421387009A | EA | 0
53 | Valid |  | I.3.9.4 |  |  |  | 1-1/2" | 1-1/2"NPT(M) x M50(F) | ED03AI99AE01ZZ10AD99ZZ | 1.5 | M421387014A | EA | 0
54 | Valid |  | I.3.9.5 |  |  |  | M20 | M20. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322G | EA | 0
55 | Valid |  | I.3.9.6 |  |  |  | M63 | M63. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 63 | M388017333F | EA | 0
56 | Valid |  | I.4 |  | REDUCER
57 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
58 | Valid |  |  |  |  | - 316SS, METRIC threaded, 'O' Ring (Male x Female)
59 | Valid |  | I.4.1 |  |  |  | M20 | M25. M x M20. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322B | EA | 0
60 | Valid |  | I.4.2 |  |  |  | M20 | M32. M x M20. F | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322C | EA | 0
61 | Valid |  | I.4.3 |  |  |  | M25 | M32. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323C | EA | 0
62 | Valid |  | I.4.4 |  |  |  | M25 | M40. M x M25. F | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323D | EA | 0
63 | Valid |  | I.4.5 |  |  |  | M32 | M40. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324D | EA | 0
64 | Valid |  | I.4.6 |  |  |  | M32 | M50. M x M32. F | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324E | EA | 0
65 | Valid |  | I.4.7 |  |  |  | M40 | M50. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325D | EA | 0
66 | Valid |  | I.4.8 |  |  |  | M40 | M63. M x M40. F | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325E | EA | 0
67 | Valid |  | I.4.9 |  |  |  | M50 | M63. M x M50. F | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326D | EA | 0
68 | Valid |  | I.5 |  | PLUG
69 | Valid |  |  |  |  | - Certified flameproof (type 'd', EEx d), IP66
70 | Valid |  |  |  |  | - 316SS, METRIC threaded
71 | Valid |  | I.5.1 |  |  |  | M20 | M20.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 20 | M388017322D | EA | 0
72 | Valid |  | I.5.2 |  |  |  | M25 | M25.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 25 | M388017323E | EA | 40 |  |  | 20 | [10 empty] | 10 | 10
73 | Valid |  | I.5.3 |  |  |  | M32 | M32.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 32 | M388017324F | EA | 40 |  |  | 20 | [10 empty] | 10 | 10
74 | Valid |  | I.5.4 |  |  |  | M40 | M40.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 40 | M388017325F | EA | 0
75 | Valid |  | I.5.5 |  |  |  | M50 | M50.M, PLUG | ED03AI99AE01ZZ10AD99ZZ | 50 | M388017326E | EA | 0
Note on Q19: HEC: Speaker, Interom Station, Camera, Wifi
Note on U19: HEC: Speaker, CCTV
Note on V19: HEC: Speaker, CCTV
Note on AB19: HEC: Speaker, Interom Station, Camera, Wifi
Note on AC19: HEC: Speaker, Interom Station, Camera, Wifi
Note on AE19: HEC: Speaker, CCTV
Note on AF19: HEC: Speaker, CCTV
Note on AV19: HEC: CCTV Camera, MBS

## Support
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | MR No. | Item | Description |  | Additional Spec. | Commodity | Support Width | Support Height | Support Thickness | Ident | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[6 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[16 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | 0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | Q |  | SUPPORT
2 | Valid |  | Q.1 |  | "U" CHANNEL (UNISTRUT CHANNEL)
3 | Valid |  | Q.1.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 41 x 41 x 2.5t | with APCS-26 Coating, For Instrument | IM23AA | 41 | 41 | 2.5 | M220652813G | M | 0
4 | Valid |  | Q.1.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 41 x 41 x 2.5t |  | IM23AA | 41 | 41 | 2.5 | M220652813 | M | 0
5 | Valid |  | Q.1.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL (Double Type) | 41 x 41 x 2.5t | (Double Type, For Instrument | IM23AA | 41 | 41 | 2.5 | M220652813H | M | 0
6 | Valid |  | Q.1.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 41 x 41 x 2.5t | with APCS-26 Coating, For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813E | M | 0
7 | Valid |  | Q.1.5 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 41 x 41 x 2.5t | For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813F | M | 0
8 | Valid |  | Q.1.6 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL (Double Type) | 82 x 82 x 2.5t | For Telecom | IM23AA | 84 | 41 | 2.6 | M421387020A | M | 0
9 | Valid |  | Q.1.7 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with PVC Coating | 41 x 41 x 2.5t | with PVC Coating, For Telecom | IM23AA | 41 | 41 | 2.5 | M220652813I | EA | 2000 | [13 empty] | 1000 | 1000
10 | Valid |  | Q.2 |  | "C" CHANNEL
11 | Valid |  | Q.2.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 100 x 50 x 5t | APCS-26 Coating, For Instrument | IM22ZZ | 100 | 50 | 5 | M206428743L | M | 0
12 | Valid |  | Q.2.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 100 x 50 x 5t | For Instrument | IM22ZZ | 100 | 50 | 5 | M206428743M | M | 0
13 | Valid |  | Q.2.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 150 x 75 x 6.5t | APCS-26 Coating, For Instrument | IM22ZZ | 150 | 75 | 6.5 | M222716891C | M | 0
14 | Valid |  | Q.2.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 100 x 50 x 5t | APCS-26 Coating, For Telecom | IM22ZZ | 100 | 50 | 5 | M206428743G | M | 1000 | [13 empty] | 500 | 500
15 | Valid |  | Q.2.5 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 75 x 75 x 5t | APCS-26 Coating , For Telecom | IM22ZZ | 75 | 75 | 5 | M206428767A | M | 0
16 | Valid |  | Q.2.6 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 125 x 65 x 5t | APCS-26 Coating, For Instrument | IM22ZZ | 125 | 65 | 5 | M414586711C | M | 0
17 | Valid |  | Q.3 |  | ANGLE
18 | Valid |  | Q.3.1 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 50 x 50 x 6t | APCS-26 Coating, For Instrument | IM21ZZ | 50 | 50 | 6 | M209850335I | M | 0
19 | Valid |  | Q.3.2 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL | 50 x 50 x 6t | For Instrument | IM21ZZ | 50 | 50 | 6 | M209850335J | M | 0
20 | Valid |  | Q.3.3 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 50 x 50 x 6t | APCS-26 Coating, For Telecom | IM21ZZ | 50 | 50 | 6 | M209850335E | M | 1000 | [13 empty] | 500 | 500
21 | Valid |  | Q.3.4 |  |  | MATERIAL : HOT DIP GALVANIZED STEEL with APCS-26 Coating | 75 x 75 x 6t | APCS-26 Coating (for Telecom) | IM21ZZ | 75 | 75 | 6 | M206428742A | M | 0
22 | Valid |  | Q.4 |  | STANCHION PIPE
23 | Valid |  |  |  |  | MATERIAL : HOT DIP GALVANIZED STEEL, 40 SCH WITH BASE PLATE, BLIND PLATE,
24 | Valid |  |  |  |  | NAMEPLATE BASE, EARTHING BOSS & GUSSET PLATE with APCS-26 coating
25 | Valid |  | Q.4.1 |  |  | Single pole Type | 2"x1600mm | 2"x1600mm | IM13ZZ |  |  |  | M206428747AY | EA | 0
26 | Valid |  | Q.4.2 |  |  | Single pole Type | 2"x700mm | 2"x700mm | IM13ZZ |  |  |  | M206428747O | EA | 0
27 | Valid |  | Q.4.3 |  |  | Single pole Type | 2"x2500mm | 2"x2500mm | IM13ZZ |  |  |  | M206428747AZ | EA | 0
28 | Valid |  | Q.4.4 |  |  | Double pole Type | 2"x1600mm | 2"x1600mm Double | IM13ZZ |  |  |  | M206428747BC | EA | 0
29 | Valid |  | Q.4.5 |  |  | Triple pole Type | 2"x1600mm | 2"x1600mm Triple | IM13ZZ |  |  |  | M206428747BD | EA | 0
30 | Valid |  | Q.4.6 |  |  | Multi Pole Type | 2"x1600mm | 2"x1600mm, TT Rack | IM13ZZ |  |  |  | M206428747BK | EA | 0
31 | Valid |  | Q.5 |  | STEEL PLATE
32 | Valid |  |  |  |  | MATERIAL : HOT DIP GALVANIZED STEEL
33 | Valid |  | Q.5.1 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 250 x 250 x 8t | 12mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 250 | 250 | 8 | M280954899C | EA | 0
34 | Valid |  | Q.5.2 |  |  | 12mmф x 2 Holes | 250 x 250 x 8t | 12mmф x 2 Holes | IM24ZZ | 250 | 250 | 8 | M280954899D | EA | 0
35 | Valid |  | Q.5.3 |  |  | 10mmф x 2 Holes (pre Fabricated) with APCS-26 Coating | 150 x 70 x 5t | 150 x 70 x 5t(base plate) + 250mm(Angle) plate) + 250mm(Angle), 10mmф x 2 Holes (pre Fabricated) with APCS-26 Coating | IM24ZZ | 150 | 70 | 5 | M349321990D | EA | 0
36 | Valid |  | Q.5.4 |  |  | 10mmф x 4 Holes with APCS-26 Coating | 100 x 100 x 5t | 10mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 100 | 100 | 5 | M280954901D | EA | 0
37 | Valid |  | Q.5.5 |  |  | (TOE Plate) with APCS-26 Coating | 125 x 2000 x 6t | (TOE Plate) with APCS-26 Coating | IM24ZZ | 125 | 2000 | 6 | M349321991B | EA | 0
38 | Valid |  | Q.5.6 |  |  | (Gusset Plate) with APCS-26 Coating | 130 x 80 x 5t | (Gusset Plate) with APCS-26 Coating | IM24ZZ | 130 | 80 | 5 | M365749317B | EA | 0
39 | Valid |  | Q.5.7 |  |  | (Name Plate Base) with APCS-26 Coating | 85 x 50 x 3t | (Name Plate Base) with APCS-26 Coating | IM24ZZ | 85 | 50 | 3 | M365749318B | EA | 0
40 | Valid |  | Q.5.8 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 400 x 210 x 6t | 12mmф x 4 Holes with APCS-26 Coating | IM24ZZ | 400 | 210 | 6 | M367575867A | EA | 0
41 | Valid |  | Q.5.9 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 250 x 250 x 8t | 12mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 250 | 250 | 8 | M280954899E | EA | 1000 | [13 empty] | 500 | 500
42 | Valid |  | Q.5.10 |  |  | 10mmф x 4 Holes with APCS-26 Coating | 100 x 100 x 5t | 10mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 100 | 100 | 5 | M280954901E | EA | 0
43 | Valid |  | Q.5.11 |  |  | 12mmф x 4 Holes with APCS-26 Coating | 350 x 350 x 10t | 12mmф x 4 Holes with APCS-26 Coating (for Telecom) | IM24ZZ | 350 | 350 | 10 | M206428755A | EA | 0
44 | Valid |  | Q.5.12 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 125 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 250 | 125 | 8 | M365749316B | EA | 0
45 | Valid |  | Q.5.13 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 70 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 250 | 70 | 8 | M414586712A | EA | 0
46 | Valid |  | Q.5.14 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 200 x 70 x 8t | 12mmф x 2 Holes with APCS-26 Coating | IM24ZZ | 200 | 70 | 8 | M414586713A | EA | 0
47 | Valid |  | Q.5.15 |  |  | (TOE PLATE) with APCS-26 Coating | 350 x 125 x 6t | (TOE PLATE) with APCS-26 Coating | IM24ZZ | 350 | 125 | 6 | M414586721A | EA | 0
48 | Valid |  | Q.5.16 |  |  | (POST PLATE) 14 mmф x 2 Holes with APCS-26 Coationg | 100 x 200 x 6t x 82 x 90 x 6 | (POST PLATE) with APCS-26 Coating | IM24ZZ | 100 | 50 | 6 | M421387021A | EA | 0
49 | Valid |  | Q.5.17 |  |  | (TOE Plate) with APCS-26 Coating | 125 x 2000 x 6t | (TOE Plate) with APCS-26 Coating (for Telecom) | IM24ZZ | 125 | 2000 | 6 | M349321991C | EA | 0
50 | Valid |  | Q.5.18 |  |  | 12mmф x 2 Holes with APCS-26 Coating | 250 x 125 x 8t | 12mmф x 2 Holes with APCS-26 Coating for Telecom | IM24ZZ | 250 | 125 | 8 | M365749316C | EA | 0
51 | Valid |  | Q.6 |  | SUNSHADE
52 | Valid |  | Q.6.1 |  |  | GRP, Bracket w/ 2" U-Bolt & Nuts, washer | NONE | GRP, Bracket w/ 2" U-Bolt & Nuts, washer, by Vendor | IM12ED |  |  |  | M349321992G | EA | 0
53 | Valid |  | Q.6.2 |  |  | GRP, (for Multi Transmitter Rack) with Bolting type | NONE | GRP, (for Multi Transmitter Rack) with Bolting type, by Vendor | IM12ED |  |  |  | M349321992H | EA | 0
54 | Valid |  | Q.6.3 |  |  | 316SS, Bracket w/ 2" U-Bolt & Nuts, washer | NONE | 316SS, Bracket w/ 2" U-Bolt & Nuts, washer, by Vendor | IM12ED |  |  |  | M349321992I | EA | 0
55 | Valid |  | Q.7 |  | NAME PLATE
56 | Valid |  |  |  |  | PHENOLIC / BAKELITE-LAMINATED PLASTIC WITH SCREWS (316SS)
57 | Valid |  | Q.7.1 |  |  | - BLACK TEXT WITH WHITE BACKGROUND FOR DCS | NONE | - BLACK TEXT WITH WHITE BACKGROUND FOR DCS | IM62ZZ |  |  |  | M220651966E | EA | 0
58 | Valid |  | Q.7.2 |  |  | - WHITE TEXT WITH RED BACKGROUND FOR ESD & FGS | NONE | - WHITE TEXT WITH RED BACKGROUND FOR ESD & FGS | IM62ZZ |  |  |  | M220651966F | EA | 0
59 | Valid |  | Q.7.3 |  |  | STAINLESS STEEL NAMEPLATE WITH BLACK TEXT FOR TAPPING POINT | NONE | STAINLESS STEEL NAMEPLATE WITH BLACK TEXT FOR TAPPING POINT | IM62ZZ |  |  |  | M220651966G | EA | 0
60 | Valid |  | Q.7.4 |  |  | TWISTED STAINLESS STEEL WIRE | NONE | TWISTED STAINLESS STEEL WIRE | IM62ZZ |  |  |  | M220651966H | EA | 0
61 | Valid |  | Q.8 |  | THREADED ROD
62 | Valid |  |  |  |  | MATERIAL : 316SS
63 | Valid |  | Q.8.1 |  |  | - 2 HEX HEAD 2 NUT & WASHER | NONE | - 2 HEX HEAD 2 NUT & WASHER | IM99EB |  |  |  | M349322107C | EA | 0
64 | Valid |  | Q.8.2 |  |  | - 2 HEX HEAD 2 NUT & WASHER | NONE | - 2 HEX HEAD 2 NUT & WASHER (for Telecom) | IM99EB |  |  |  | M349322107E | EA | 0
65 | Valid |  | Q.9 |  | THREADED ROD COUPLING
66 | Valid |  | Q.9.1 |  |  | MATERIAL : 316SS | NONE | MATERIAL : 316SS | IM99EB |  |  |  | M349322107D | EA | 0
67 | Valid |  | Q.9.2 |  |  | MATERIAL : 316SS | NONE | MATERIAL : 316SS (for Telecom) | IM99EB |  |  |  | M349322107F | EA | 0
68 | Valid |  | Q.10 |  | HILTI FASTNER W/NUTS
69 | Valid |  | Q.10.1 |  |  | 316SS, X-BT-R | NONE | 316SS, X-BT-R | IM41EA |  |  |  | M206340618GI | SET | 0
70 | Valid |  | Q.10.2 |  |  | 316SS, X-BT-R | NONE | 316SS, X-BT-R (for Telecom) | IM41EA |  |  |  | M206340618TC | SET | 0
71 | Valid |  | Q.11 |  | HILTI EXTEND ADAPTOR
72 | Valid |  | Q.11.1 |  |  | Item no. 387224 | NONE | Item no. 387224 | IM41EA |  |  |  | M206340618GJ | SET | 0
73 | Valid |  | Q.12 |  | SPACER for DUCT BANK
74 | Valid |  | Q.12.1 |  |  | CONDUIT 150mm BASE SPACERS | NONE | 6" BASE | IM99ZZ |  |  |  | M206396958HG | EA | 0
75 | Valid |  | Q.12.2 |  |  | CONDUIT 150mm INTERMEDIATE SPACERS | NONE | 6" INTERMEDIATE | IM99ZZ |  |  |  | M206396958HH | EA | 0
76 | Valid |  | Q.12.3 |  |  | CONDUIT 100mm BASE SPACERS | NONE | 4" BASE (forTelecom) | IM99ZZ |  |  |  | M206396958KX | EA | 0
77 | Valid |  | Q.12.4 |  |  | CONDUIT 100mm INTERMEDIATE SPACERS | NONE | 4" INTERMEDIATE (for Telecom) | IM99ZZ |  |  |  | M206396958KY | EA | 0
78 | Valid |  | Q.13 |  | END BELL (BELLMOUSE)
79 | Valid |  | Q.13.1 |  |  | Fitting for NEMA TC8 TYPE PVC conduit shall be in accordance with NEMA TC9, Color Grey | NONE | Fitting for NEMA TC8 TYPE PVC conduit shall be in accordance with NEMA TC9, Color Grey | IM99ZZ |  |  |  | M206396958FN | EA | 0
80 | Valid |  | Q.13.2 |  |  | Fitting for NEMA TC2 Type PVC conduit shall be in accordance with NEMA TC3, Color Grey | NONE | Fitting for NEMA TC2 Type PVC conduit shall be in accordance with NEMA TC3, Color Grey | IM99ZZ |  |  |  | M206396958FM | EA | 0
81 | Valid |  | Q.14 |  | End PLUG for PVC Conduit (Rubber PLUG for PVC Conduit) (FOR TELECOM DUCT BANK)
82 | Valid |  | Q.14.1 |  |  |  | NONE | END PLUG FOR 4" for Telecom | IM15ZZ |  |  |  | M206327315D | EA | 0
83 | Valid |  | Q.14.2 |  |  |  | NONE | END PLUG FOR 6" | IM15ZZ |  |  |  | M206327315C | EA | 0
84 | Valid |  | Q.15 |  | Quadplex Duct Plug for Sub-duct (FOR TELECOM DUCT BANK)
85 | Valid |  | Q.15.1 |  |  |  | NONE | Duct plug for 4" | IM99ZZ |  |  |  | M206396958HJ | EA | 0
86 | Valid |  | Q.16 |  | Simplex Sub Duct Plug (FOR TELECOM DUCT BANK)
87 | Valid |  | Q.16.1 |  |  |  | NONE | Duct plug for 1" (for Telecom) | IM99ZZ |  |  |  | M206396958KZ | EA | 0
88 | Valid |  | Q.17 |  | EARTH BOSS
89 | Valid |  |  |  |  | HOT DIP GALVANIZED STEEL, APCS-26 Coating
90 | Valid |  | Q.17.1 |  |  | (pre-welded at Stanchion pipe and else to be supplied separately for site installation.) | NONE | 30mmф x 30mm(L) x M12 | IM99ZZ |  |  |  | M206396958FU | EA | 0
91 | Valid |  | Q.18 |  | PULL BOX FOR TELECOM
92 | Valid |  | Q.18.1 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 100mmx405mmx75mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789A | EA | 0
93 | Valid |  | Q.18.2 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 150mmx510mmx75mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789B | EA | 0
94 | Valid |  | Q.18.3 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 102mmx102mmx54mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789C | EA | 174 | [16 empty] | 88 | 86
95 | Valid |  | Q.18.4 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 200mm x 686 mm x 75 mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789D | EA | 0
96 | Valid |  | Q.18.5 |  |  | HOT DIP GALVANIZED CARBON STEEL | - | 250mm x 686 mm x 75 mm | EJ02ZZ99AA01AA99AG99 |  |  |  | M367577789E | EA | 0
97 | Valid |  | Q.19 |  | CABLE MARKER POST (FOR TELECOM CABLE)
98 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036897-001
99 | Valid |  |  |  |  | - FIBER GLASS, ORANGE COLOR
100 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
101 | Valid |  |  |  |  | - 120mm x 100mm x 1400mm
102 | Valid |  | Q.19.1 |  |  |  | NONE | TE, POST, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186X | EA | 0
103 | Valid |  | Q.19.2 |  |  |  | NONE | TE, POST, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186Y | EA | 0
104 | Valid |  | Q.19.3 |  |  |  | NONE | TE, POST, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186Z | EA | 0
105 | Valid |  | Q.19.4 |  |  |  | NONE | TE, POST, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AA | EA | 0
106 | Valid |  | Q.19.5 |  |  |  | NONE | TE, POST, SIGN TYPE "E" | IM35ZZ |  |  |  | M201587186AB | EA | 0
107 | Valid |  | Q.19.6 |  |  |  | NONE | MARKER POST | IM35ZZ |  |  |  | M201587186AT | EA | 0
108 | Valid |  | Q.20 |  | SURFACE MARKER (FOR TELECOM CABLE)
109 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036273-001
110 | Valid |  |  |  |  | - CONCRETE SLAB
111 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
112 | Valid |  |  |  |  | - 305mm x 305mm x 76mm
113 | Valid |  | Q.20.1 |  |  |  | NONE | TE, MARKER, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AC | EA | 0
114 | Valid |  | Q.20.2 |  |  |  | NONE | TE, MARKER, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AD | EA | 0
115 | Valid |  | Q.20.3 |  |  |  | NONE | TE, MARKER, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AE | EA | 0
116 | Valid |  | Q.20.4 |  |  |  | NONE | TE, MARKER, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AF | EA | 0
117 | Valid |  | Q.20.5 |  |  |  | NONE | CONCRETE SLAB | IM35ZZ |  |  |  | M201587186N | EA | 0
118 | Valid |  | Q.21 |  | WARNING TAPE (FOR TELECOM CABLE)
119 | Valid |  |  |  |  | - ORANGE COLOR
120 | Valid |  | Q.21.1 |  |  | DETECTABLE MARKER TAPE | NONE | TE, DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AG | m | 0
121 | Valid |  | Q.21.2 |  |  | NON-DETECTABLE MARKER TAPE | NONE | TE, NON-DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AH | m | 0
122 | Valid |  | Q.22 |  | CABLE MARKER POST (FOR INSTRUMENT CABLE)
123 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036326-001
124 | Valid |  |  |  |  | - RED WOOD
125 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
126 | Valid |  |  |  |  | - 100mm x 100mm x 1370mm
127 | Valid |  | Q.22.1 |  |  |  | NONE | CI, POST, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AI | EA | 0
128 | Valid |  | Q.22.2 |  |  |  | NONE | CI, POST, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AJ | EA | 0
129 | Valid |  | Q.22.3 |  |  |  | NONE | CI, POST, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AK | EA | 0
130 | Valid |  | Q.22.4 |  |  |  | NONE | SIGN-POST | IM35ZZ |  |  |  | M201587186BN | EA | 0
131 | Valid |  | Q.23 |  | SURFACE MARKER (FOR INSTRUMENT CABLE)
132 | Valid |  |  |  |  | - COMPLY WITH STANDARD DRAWING AB-036273-001
133 | Valid |  |  |  |  | - CONCRETE SLAB
134 | Valid |  |  |  |  | - INCLUDING SIGN PLATES (ENGRACED, SOLID BLACK ON YELLOW BLACK-GROUND)
135 | Valid |  |  |  |  | - 305mm x 305mm x 76mm
136 | Valid |  | Q.23.1 |  |  |  | NONE | CI, MARKER, SIGN TYPE "A" | IM35ZZ |  |  |  | M201587186AL | EA | 0
137 | Valid |  | Q.23.2 |  |  |  | NONE | CI, MARKER, SIGN TYPE "B" | IM35ZZ |  |  |  | M201587186AM | EA | 0
138 | Valid |  | Q.23.3 |  |  |  | NONE | CI, MARKER, SIGN TYPE "C" | IM35ZZ |  |  |  | M201587186AN | EA | 0
139 | Valid |  | Q.23.4 |  |  |  | NONE | CI, MARKER, SIGN TYPE "D" | IM35ZZ |  |  |  | M201587186AO | EA | 0
140 | Valid |  | Q.23.5 |  |  |  | NONE | CABLE MARKER(PLAQUE) | IM35ZZ |  |  |  | M201587186BO | EA | 0
141 | Valid |  | Q.24 |  | WARNING TAPE (FOR INSTRUMENT CABLE)
142 | Valid |  |  |  |  | - YELLOW COLOR
143 | Valid |  | Q.24.1 |  |  | DETECTABLE MARKER TAPE | NONE | CI, DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AP | M | 0
144 | Valid |  | Q.24.2 |  |  | NON-DETECTABLE MARKER TAPE | NONE | CI, NON-DETECTABLE MARKER TAPE | IM35ZZ |  |  |  | M201587186AQ | M | 0
145 | Valid |  | Q.25 |  | ELECTRONINC MARKER SYSTEM (FOR TELECOM CABLE)
146 | Valid |  | Q.25.1 |  |  | ELECTRONINC MARKER SYSTEM | NONE | (for Telecom) | IM35ZZ |  |  |  | M201587186AS | EA | 0
141 | Valid |  | Q.26 |  | PLYWOOD BACKBOARDS
142 | Valid
143 | Valid |  | Q.26.1 |  |  | 7 INCHES BY EIGHT (8) FEET BY FOUR (4) PAINTED WITH TWO (2) COATS, FIRE-RETARDANT WHITE PAINT | NONE | 7 INCHES BY EIGHT (8) FEET BY FOUR (4) PAINTED WITH TWO (2) COATS, FIRE-RETARDANT WHITE PAINT | IM35ZZ |  |  |  | M201587186AP | EA | 8 | [6 empty] | 2 | 2 | [8 empty] | 2 | 2
Note on AG99: HEC: 50 for Data outlet (assumed) 38 for Security (as per IFB drawing)
Note on AH99: HEC: 50 for Data outlet (assumed) 38 for Security (as per IFB drawing)

## Telecom & Security System
[TE] Data Input/View
As of 2026-07-31
SN | Status | Message | Item No. | Item | Description |  | Tag No | Material Master | Height | Core/Pair Number | Composition | MR No. | Unit | Total Q'ty | PKG-1 | [12 empty] | PKG-2 | [20 empty] | Remark
[5 empty] | Specification | Size | [8 empty] | Common-1 | Common-2 | EB HCKR Train1&2 | EB Fractionation | EB Integrated DHT & Compressors | EB Catalyst Loading & Common | SS-071 | PIB-080 | HRU | CWS | SS-070 | PKG1 PCS in Existing CCR | Green Zone Fence - BOTB Plot | SRU | ARU | SWS | SS-072 | PIB-081 | Flare System with Existing SS-052 & SS-046 Mod | Sales Gas Pipeline | Caustic Pump with Existing PIB-02 & SS-013 Mod | SW Pump with Existing PIB-13 & SS-026 Mod | OSBL Pipe Racks & Interconnect pipe rack | Modifications in RAWEC SS-200 | Modifications in Existing CCR | Piping Tie-ins | Communications ¦ CCR-1 | Security ¦ CCR-3 | Communications ¦ PUCCR | Security ¦ SCC | Security ¦ ID OFFICE BLDG | Communications ¦ PIB-027 | Security ¦ WR-617 | Security ¦ Sales Gas P/L Scraper Launcher Area
[15 empty] | CWA-XXXX | CWA-XXXX | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0101 | CWA-0102 | CWA-0103 | CWA-0300 | CWA-0600 | CWA-1300 | CWA-1500 | CWA-2400 | CWA-0201 | CWA-0202 | CWA-0203 | CWA-0204 | CWA-0205 | CWA-0700 | CWA-0900 | CWA-1000 | CWA-1100 | CWA-1200 | CWA-1400 | CWA-1500 | CWA-1600 | CWA-1800 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100 | CWA-1800 | CWA-2100 | CWA-2100
1 | Valid |  | S | Telecommunication and Security | [5 empty] | 0
2 | Valid |  | S.1 | TELECOM SYSTMEM (IT) | [5 empty] | 0
3 | Valid |  | S.1.1 | Data Network System | [5 empty] | 0
4 | Valid |  | S.1.1.1 | Data Network System Rack | [5 empty] | 0
5 | Valid |  | S.1.1.1.1 | Data Network System Oepn Rack | 19" Open Frame Rack (42U) | 0 | S.1.1.1.1 | FI31CC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 8 | [7 empty] | 2 | [9 empty] | 2 | [8 empty] | 2 |  | 2 | [6 empty] | Updated based on main equipment data: 42U ACS/CCTV and Security cabinets (and CCR-1/3 worst-case rack provisions).
6 | Valid |  | S.1.1.1.2 | Data Network System Wall Mount Rack | 19" Swing Gate Wall Mount Rack (14U): CUBE-IT | 0 | S.1.1.1.2 | FI31CB00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [18 empty] | Worst-case scenario provision: New 12U/14U security enclosure to house FPPs and switches if rearrangement of existing cabinets yields no space.
7 | Valid |  | S.1.1.1.3 | Data Network System Ethernet Switch | Layer 2 (Layer 3 compatible) LAN Access Switches (with PoE+ capability) (Modification) Existing CISCO CATALYST 9500 DISTRIBUTION SWITCH |  | S.1.1.1.3 |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [26 empty] | 2
8 | Valid |  | S.1.1.1.3.1 | Data Network System 24 port Ethernet Switch | 24 port Ethernet Switch | 0 | S.1.1.1.3.1 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Worst-case scenario provision: Ethernet switches, converters, and gateways to interface with existing control systems.
9 | Valid |  | S.1.1.1.3.2 | Data Network System 48 port Modular type Ethernet Switch | 48 port Modular type Ethernet Switch | 0 | S.1.1.1.3.2 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Worst-case scenario provision: New Catalyst 4510+E line cards or switch if no spare ports exist.
10 | Valid |  | S.1.1.1.3.3 | Data Network System 48 port Ethernet Switch | 48 port Ethernet Switch | 0 | S.1.1.1.3.3 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [18 empty] | Horizontal Cabling
11 | Valid |  | S.1.1.1.3.4 | Data Network System 72 port Modular Ethernet Switch | 96 port Modular Ethernet Switch | 0 | S.1.1.1.3.4 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 | [7 empty] | 2 | [9 empty] | 2
12 | Valid |  | S.1.1.1.3.5 | Data Network System 144 port Modular type Ethernet switch | 108 port Modular type Ethernet switch | 0 | S.1.1.1.3.5 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
13 | Valid |  | S.1.1.1.4 | Data Network System SFP Transceiver for switch | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.1.1.4 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [6 empty] | 2 | 4 |  |  | 2 | [5 empty] | 2 | 4
14 | Valid |  | S.1.1.1.5 | Data Network System SFP+ Transceiver for switch | 10G SFP+ LC LR SMF transciever for Aruba switch | 0 | S.1.1.1.5 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
15 | Valid |  | S.1.1.1.6 | Data Network System SFP Transceiver for router | 1G SFP LC LX SMF transciever for Juniper PE router | 0 | S.1.1.1.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
16 | Valid |  | S.1.1.1.7 | Data Network System SFP+ Transceiver for router | 10G SFP+ LC LR SMF transciever for Juniper PE router | 0 | S.1.1.1.7 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
17 | Valid |  | S.1.1.1.8 | Data Network System Power Receptacles | 230VAC, 20A, duplex | 0 | S.1.1.1.8 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 10 | [6 empty] | 2 | 2 |  |  | 2 | [5 empty] | 2 | 2 | [17 empty] | SAES-T-916
18 | Valid |  | S.1.1.1.9 | Data Network System Fiber Optic Patch Panel |  |  | S.1.1.1.9 |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
19 | Valid |  | S.1.1.1.9.1 | Data Network System 24 Port Fiber Optic Patch Panel | 24 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.1 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 6 | [6 empty] | 2 |  |  |  | 2 | [5 empty] | 2 | [18 empty] | Worst-case scenario provision: 1 FPP in CCR-1 & 1 FPP in CCR-3. New buildings and areas updated based on FOPP Take-Off: SS-070: 12 FPPs, PIB-080: 2 FPPs, SS-071: 17 FPPs, PKG-2 Common: 6 FPPs, SS-072: 19 FPPs, PIB-081: 9 FPPs, CCR-3: 1 FPP, PIB-027: 1 FPP. FOPPs supplied as complete sets including chassis, splice trays, SC/LC adapters, SM pigtails, glands, and UMS mounting profiles.
20 | Valid |  | S.1.1.1.9.2 | Data Network System 48 Port Fiber Optic Patch Panel | 48 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Worst-case scenario provision: 1 FPP in CCR-3. Quantities updated based on FOPP Take-Off: PIB-080: 6 FPPs, PIB-081: 4 FPPs, CCR-1: 6 FPPs. FOPPs supplied as complete sets including chassis, splice trays, SC/LC adapters, SM pigtails, glands, and UMS mounting profiles.
21 | Valid |  | S.1.1.1.9.3 | Data Network System 144 Port Fiber Optic Patch Panel | 144 Port Fiber Optic Patch Panel | 0 | S.1.1.1.9.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Quantities updated based on FOPP Take-Off: PUCCR: 2 FPPs for IT Network Backbone. FOPPs supplied as complete sets including chassis, splice trays, SC/LC adapters, SM pigtails, glands, and UMS mounting profiles.
| Valid |  | S.1.1.1.9.4 | Data Network System 12 Port Fiber Optic Patch Panel | 12 Port Fiber Optic Patch Panel |  | S.1.1.1.9.4 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Quantities updated based on FOPP Take-Off: EB Complex: 6 FPPs (CEMS/PSA), SS-070: 6 FPPs (PSA/PMS), PIB-080: 17 FPPs (PAS/DCS), PKG-2 Common: 13 FPPs (CEMS/PSA), PIB-081: 3 FPPs (Analyzers/PAS/FA), CCR-1: 10 FPPs (PSA/PMS). FOPPs supplied as complete sets including chassis, splice trays, SC/LC adapters, SM pigtails, glands, and UMS mounting profiles.
| Valid |  | S.1.1.1.9.5 | Data Network System 6 Port Fiber Optic Patch Panel | 6 Port Fiber Optic Patch Panel |  | S.1.1.1.9.5 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | FO PCCTV System
| Valid |  | S.1.1.1.9.6 | Data Network System 96 Port Fiber Optic Patch Panel | 96 Port Fiber Optic Patch Panel |  | S.1.1.1.9.6 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 12 | [7 empty] | 4 | [9 empty] | 4 | [8 empty] | 2 |  | 2 | [6 empty] | Worst-case scenario provision: 1 FPP in CCR-3. Quantities updated based on FOPP Take-Off: PIB-080: 9 FPPs, PIB-081: 10 FPPs, CCR-1: 9 FPPs, PUCCR: 5 FPPs. FOPPs supplied as complete sets including chassis, splice trays, SC/LC adapters, SM pigtails, glands, and UMS mounting profiles.
22 | Valid |  | S.1.1.1.10 | Data Network System UTP Patch Panel | including Front RJ45 'Snap-in' type connectors with clear plastic indetification labels |  | S.1.1.1.10 |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
23 | Valid |  | S.1.1.1.10.1 | Data Network System 24 Port UTP Patch panel | 24 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.1 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Horizontal Cabling
24 | Valid |  | S.1.1.1.10.2 | Data Network System 48 Port UTP Patch panel | 48 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 |  |  |  | 1 | [5 empty] | 1
25 | Valid |  | S.1.1.1.10.3 | Data Network System 72 Port UTP Patch panel | 96 Port UTP Patch panel, Cat6A | 0 | S.1.1.1.10.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [7 empty] | 1 | [9 empty] | 1
26 | Valid |  | S.1.1.2 | Data Network System Uninterruptible Power Supply(UPS) | Rack mountable type with a minimum of 2 hours UPS autonomy |  | S.1.1.2 |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
27 | Valid |  | S.1.1.2.1 | Data Network System Rack mountable ATS (Auotomatic Tranfer Switch) | ATS | 0 | S.1.1.2.1 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
28 | Valid |  | S.1.1.2.2 | Data Network System 3kVA UPS | 3kVA UPS | 0 | S.1.1.2.2 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 | 1 |  |  | 1
29 | Valid |  | S.1.1.2.3 | Data Network System 5kVA UPS | 3.5kVA UPS | 0 | S.1.1.2.3 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [16 empty] | 1 | 1
30 | Valid |  | S.1.1.2.4 | Data Network System 8kVA UPS | 8kVA UPS | 0 | S.1.1.2.4 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
31 | Valid |  | S.1.1.2.5 | Data Network System 10kVA UPS | 10kVA UPS | 0 | S.1.1.2.5 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
32 | Valid |  | S.1.1.2.6 | Data Network System Battery Packs | Battery Pack for 3kVA UPS | 0 | S.1.1.2.6 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [6 empty] | 1 | 1 |  |  | 1
33 | Valid |  | S.1.1.2.7 | Data Network System Battery Packs | Battery Pack for 3.5kVA UPS | 0 | S.1.1.2.7 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [16 empty] | 1 | 1
34 | Valid |  | S.1.1.2.8 | Data Network System Battery Packs | Battery Pack for 10kVA UPS | 0 | S.1.1.2.8 | FU81ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | UPS battery packs for target building telecom racks (1 per building for SS-070, PIB-080, SS-071, SS-072, PIB-081) to support our 5 taken-off 3kVA UPS units (1-to-1 dependency). Backup runtime sized for 30/60 minutes.
35 | Valid |  | S.1.1.3 | Data Network System Patch Cords | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
36 | Valid |  | S.1.1.3.1 | Data Network System UTP Patch cord (1.5m) | UTP Patch cord (1.5m), Cat.6A | 0 | S.1.1.3.1 | FI37HC02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 50 | [6 empty] | 10 | 10 |  |  | 10 | [5 empty] | 10 | 10 | [17 empty] | Worst-case scenario provision: 48 UTP patch cords in CCR-1 & CCR-3 to patch switch ports. For new buildings, provides 1.5m Cat.6A patch cords in the Telecom Rooms to connect all horizontal UTP runs from the UTP patch panels to the LAN access switches and voice distribution system (SS-070: 18, PIB-080: 120, SS-071: 22, SS-072: 14, PIB-081: 22).
37 | Valid |  | S.1.1.3.2 | Data Network System Fiber Optic Patch cord (1.5m) | Fiber Optic Patch cord (1.5m) | 0 | S.1.1.3.2 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 120 | [6 empty] | 20 | 20 |  |  | 20 | [5 empty] | 20 | 20 | [8 empty] | 10 |  | 10 | [6 empty] | Worst-case scenario provision: SC-LC and SC-SC fiber patch cords to terminate new links in CCR-3 (96 sets). Quantities for other locations aligned with FOPPs (1 duplex patch cord set per 2 ports): EB Complex: 36, SS-070: 180, PIB-080: 750, SS-071: 204, PKG-2 Common: 150, SS-072: 228, PIB-081: 702, CCR-1: 648, PUCCR: 384, PIB-027: 12.
38 | Valid |  | S.1.1.3.3 | Data Network System Fiber Optic Patch cord (15m) | Fiber Optic Patch cord (15m) | 0 | S.1.1.3.3 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 70 | [6 empty] | 10 | 10 |  |  | 10 | [5 empty] | 10 | 10 | [8 empty] | 10 |  | 10
39 | Valid |  | S.1.1.4 | Data Network System Telecom enclosure with switch | for PSA FOC Splice |  |  |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
40 | Valid |  | S.1.1.4.1 | Data Network System Ethernet switch | Ethernet Switch (24 port) if any | 0 | S.1.1.4.1 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
41 | Valid |  | S.1.1.4.2 | Data Network System SFP Transceiver | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.1.4.2 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
42 | Valid |  | S.1.1.4.3 | Data Network System Fiber Optic Patch Panel (DIN, 4port) | Fiber Optic Patch Panel (Rac Mount, 12port) | 0 | S.1.1.4.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
43 | Valid |  | S.1.1.4.4 | Data Network System Fiber Optic Patch Panel (DIN, 4port) | Fiber Optic Patch Panel (Rac Mount, 24port) | 0 | S.1.1.4.4 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
44 | Valid |  | S.1.1.4.5 | Data Network System Telecom enclosure | Telecom enclosure Size: 1525h x 575w x 300d | 0 | S.1.1.4.5 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
45 | Valid |  | S.1.1.4.6 | Data Network System Cat.6 Surge Protector | Cat.6 Surge Protecto (8port, DIN) | 0 | S.1.1.4.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
46 | Valid |  | S.1.1.4.7 | Data Network System Cat.6 Surge Protector | Thin Cabinet for Telecom | 0 | S.1.1.4.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
47 | Valid |  | S.1.2 | Telephone System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
48 | Valid |  | S.1.2.1 | Telephone System Basic Wall Mount IP Telephone |  | 0 | S.1.2.1 | FI33EF11ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 23 | [6 empty] | 7 | 4 |  |  | 6 | [5 empty] | 3 | 3
49 | Valid |  | S.1.2.2 | Telephone System Desktop IP Telephone |  | 0 | S.1.2.2 | FI33EF12ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 49 | [6 empty] | 2 | 42 |  |  | 1 | [5 empty] | 1 | 3
50 | Valid |  | S.1.2.3 | Telephone System Secretary IP Telephone handset | Secretary IP Telephone handset | 0 | S.1.2.3 | FI33EF12ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
51 | Valid |  | S.1.2.4 | Telephone System Meeting Room IP Conference Telephone handsets | Meeting Room IP Conference Telephone handsets | 0 | S.1.2.4 | FI33EF13ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
52 | Valid |  | S.1.2.5 | Telephone System VOIP Gateway | For Analoge Telephone to IP | 0 | S.1.2.5 | FI33EI00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
|  |  | S.1.2.6 | Telephone System Basic Wall Mount IP Telephone | Weatherproof Type | [7 empty] | SETS | 1 | [33 empty] | 1 | Assumption, TBD
53 | Valid |  | S.1.3 | pLTE Radio System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
54 | Valid |  | S.1.3.1 | Indoor Radio Repeating System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
55 | Valid |  | S.1.3.1.1 | Indoor Radio Repeating System Indoor Radio Repearter | Small Cell / eNodeB | 0 | S.1.3.1.1 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
56 | Valid |  | S.1.3.1.2 | Indoor Radio Repeating System LTE Indoor antenna | Repeating Antenna | 0 | S.1.3.1.2 | FI36GE11ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
57 | Valid |  | S.1.3.1.3 | Indoor Radio Repeating System Coaxial 2 Way Splitter | Coaxial 2 Way Splitter | 0 | S.1.3.1.3 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
58 | Valid |  | S.1.3.1.4 | Indoor Radio Repeating System Coaxial Cable 1/2" | Coaxial Cable 1/2" | 0 | S.1.3.1.4 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 1000 | [6 empty] | 200 | 200 |  |  | 200 | [5 empty] | 200 | 200
59 | Valid |  | S.1.3.1.5 | Indoor Radio Repeating System Fiber Optic patch cord(15m) | Fiber Optic Patch cord (SC/APC, 15m) | 0 | S.1.3.1.5 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
60 | Valid |  | S.1.3.1.6 | Indoor Radio Repeating System Fiber Optic patch cord(10m) | Fiber Optic Patch cord (SC/APC, 10m) | 0 | S.1.3.1.6 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
61 | Valid |  | S.1.3.1.7 | Indoor Radio Repeating System Power cord(10m) | Power cord (10m) | 0 | S.1.3.1.7 | FI37HG02ZZ-0000001 | 0 | 2 | C | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
62 | Valid |  | S.1.3.1.8 | Indoor Radio Repeating System DC Block | DC Block | 0 | S.1.3.1.8 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
63 | Valid |  | S.1.3.1.9 | Indoor Radio Repeating System Attenuator | 10dB Attenuator | 0 | S.1.3.1.9 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
64 | Valid |  | S.1.3.1.9.2 | Indoor Radio Repeating System Attenuator | 3dB Attenuator | 0 | S.1.3.1.9.2 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
65 | Valid |  | S.1.3.1.9.3 | Indoor Radio Repeating System Attenuator | 6dB Attenuator | 0 | S.1.3.1.9.3 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
66 | Valid |  | S.1.3.1.10 | Indoor Radio Repeating System SFP Transceiver | SFP Transceiver | 0 | S.1.3.1.10 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
67 | Valid |  | S.1.3.1.11 | Indoor Radio Repeating System SFP Transceiver | 12 SC/APC Simpled Splicing Casette | 0 | S.1.3.1.11 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
68 | Valid |  | S.1.3.1.12 | Accessorfies for Indoor Repater System | 272 NM, 42 NF, 21 DM Connectors and 72 Mounting Plates | 0 | S.1.3.1.12 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | Lot | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
69 | Valid |  | S.1.3.1.13 | Indoor Radio Repeating System 6dB Tapper | 6dB Tapper | 0 | S.1.3.1.13 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
70 | Valid |  | S.1.3.1.14 | Indoor Radio Repeating System 8dB Tapper | 8dB Tapper | 0 | S.1.3.1.14 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
71 | Valid |  | S.1.3.1.15 | Indoor Radio Repeating System 10dB Tapper | 10dB Tapper | 0 | S.1.3.1.15 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
72 | Valid |  | S.1.3.1.16 | Indoor Radio Repeating System 15dB Tapper | 15dB Tapper | 0 | S.1.3.1.16 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
73 | Valid |  | S.1.3.2 | Portable Radio System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
74 | Valid |  | S.1.3.2.1 | Portable Radio System Handheld Portable Radio | Handheld Portable Radio | 0 | S.1.3.2.1 | FI36GH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 100 | [7 empty] | 100
75 | Valid |  | S.1.3.2.2 | Portable Radio System Vehicle Mounted Radio | Vehicle Mounted Radio | 0 | S.1.3.2.2 | FI36GH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 7 | [7 empty] | 7
76 | Valid |  | S.1.3.3 | Fixed Radio System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
77 | Valid |  | S.1.3.3.1 | Fixed Radio System LTE Desk-top Terminal | MCPTT-enabled | 0 | S.1.3.3.1 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
78 | Valid |  | S.1.3.3.2 | Fixed Radio System Radio Interface Unit | MCPTT Client Software | 0 | S.1.3.3.2 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
79 | Valid |  | S.1.3.3.3 | Fixed Radio System RRU(Remote Radio Unit) | Audio Interface Unit / USB Controller / Dispatch Console | 0 | S.1.3.3.3 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
80 | Valid |  | S.1.3.3.4 | Fixed Radio System Outdoor Antenna | LTE Outdoor MIMO Antenna (2x2 / 4x4) | 0 | S.1.3.3.4 | FI36GE11ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 19 | [6 empty] | 3 | 5 |  |  | 3 | [5 empty] | 3 | 5 | [17 empty] | Assumption ¦ HOLD
81 | Valid |  | S.1.3.3.5 | Fixed Radio System Pole for Outdoor Antenna | Pole for Outdoor Antenna | 0 | S.1.3.3.5 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 19 | [6 empty] | 3 | 5 |  |  | 3 | [5 empty] | 3 | 5 | [17 empty] | Assumption ¦ HOLD
82 | Valid |  | S.1.3.3.6 | Fixed Radio System Surge Protector for Antenna | Surge Protector for Antenna | 0 | S.1.3.3.6 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 19 | [6 empty] | 3 | 5 |  |  | 3 | [5 empty] | 3 | 5 | [17 empty] | Assumption ¦ HOLD
83 | Valid |  | S.1.3.3.7 | Fixed Radio System 19" Open Frame Rack | 19" Open Frame Rack (if any) | 0 | S.1.3.3.7 | FI36GA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
84 | Valid |  | S.1.3.3.8 | Fixed Radio System Coaxial Cable 1/2" | LMR400 / 1/2” | 0 | S.1.3.3.8 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 1000 | [6 empty] | 200 | 200 |  |  | 200 | [5 empty] | 200 | 200 | [17 empty] | Assumption ¦ HOLD
85 | Valid |  | S.1.3.3.9 | Fixed Radio System Surge Protector Grounding Bracket | Grounding Kit (RF + Network) | 0 | S.1.3.3.9 | FI36GG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
86 | Valid |  | S.1.3.3.10 | Fixed Radio System Structured Cabling | Cat6A UTP | 0 | S.1.3.3.10 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
87 | Valid |  | S.1.3.3.11 | Fixed Radio System 24port Ethernet switch | L2/L3 Managed Switch (PoE optional) | 0 | S.1.3.3.11 | FI31CE03ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 5 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1
88 | Valid |  | S.1.3.3.12 | Fixed Radio System Programming Kit | Device Management SW / SIM Provisioning Tool | 0 | S.1.3.3.12 | FI36GM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
89 | Valid |  | S.1.4 | Wireless LAN(WLAN) System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
90 | Valid |  | S.1.4.1 | Wireless LAN System Wireless Access Points | Wireless Access Points | 0 | S.1.4.1 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 27 | [6 empty] | 6 | 8 |  |  | 5 | [5 empty] | 4 | 4
91 | Valid |  | S.1.4.2 | Wireless LAN System Explosion Proof Wireless Access Points | Explosion Proof Wireless Access Points | 0 | S.1.4.2 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
92 | Valid |  | S.1.4.3 | Wireless LAN System Hi-POE Injector | For explosion proof WLAN access points | 0 | S.1.4.3 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
93 | Valid |  | S.1.5 | Industrial Wi-Fi SYSTEM | Wi-Fi 6 or above |  |  |  |  | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
94 | Valid |  | S.1.5.1 | Industrial Wi-Fi SYSTEM Industrial Wi-Fi access points | Industrial Wi-Fi access points | 0 | S.1.5.1 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
95 | Valid |  | S.1.5.2 | Industrial Wi-Fi SYSTEM Explosion proof Industrial Wi-Fi access point | Explosion proof Industrial Wi-Fi access point | 0 | S.1.5.2 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1
96 | Valid |  | S.1.5.3 | Industrial Wi-Fi SYSTEM External Antenna for WIFI access point | External Antenna for WIFI access point | 0 | S.1.5.3 | FI33EE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
97 | Valid |  | S.1.5.4 | Industrial Wi-Fi SYSTEM WIFI antenna extension cable | WIFI antenna extension cable | 0 | S.1.5.4 | FI37HG01ZZ-0000001 | 0 | 2 | C | BOTB-PKG1-MR-TE-0001 | M | 0
98 | Valid |  | S.1.5.5 | Industrial Wi-Fi SYSTEM 5m Pole for Antenna for WIFI | 5m Pole for WIFI Access Point | 0 | S.1.5.5 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1
99 | Valid |  | S.1.5.6 | Industrial Wi-Fi SYSTEM 6m Pole for Antenna for WIFI | 6m Pole for Antenna for WIFI, ASCE-7-05, 155km/h | 0 | S.1.5.6 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
100 | Valid |  | S.1.5.6.1 | Industrial Wi-Fi SYSTEM 6m Pole for Explosion Antenna for WIFI | 6m Pole for Antenna for WIFI, ASCE-7-05, 155km/h | 0 | S.1.5.6.1 | FI33EQ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
101 | Valid |  | S.1.5.7 | Industrial Wi-Fi SYSTEM Cat.6A surge protector | Cat.6A surge protector | 0 | S.1.5.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1
102 | Valid |  | S.1.5.8 | Industrial Wi-Fi SYSTEM Enclousure for Industrial Ethernet Switch | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
103 | Valid |  | S.1.5.8.1 | Industrial Wi-Fi SYSTEM Industrial Ethernet Switch (4 port) | POE Injector (Normal Installation) | 0 | S.1.5.8.1 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
104 | Valid |  | S.1.5.8.2 | Industrial Wi-Fi SYSTEM Explosion proof Industrial Ethernet Media Converter | POE Injector (Hazard Area Installation) | 0 | S.1.5.8.2 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1
105 | Valid |  | S.1.5.8.3 | Industrial Wi-Fi SYSTEM Enclousure | Enclousure (400 x 400 x 100) | 0 | S.1.5.8.3 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0 | [35 empty] | Outdoor junction boxes containing UPS, FPP, and power connections for each IAP. Quantities updated: SS-070 Area: 1, SS-071 Area: 1, PKG-2 Common: 7. Note: Split between standard and explosion-proof models to be finalized during detailed design.
106 | Valid |  | S.1.5.8.4 | Industrial Wi-Fi SYSTEM Explosion proof Enclousure c/w FOPP | Explosion proof Enclousure (400 x 400 x 100) | 0 | S.1.5.8.4 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1 |  | To be determined (TBD) during detailed design based on hazardous area classifications.
107 | Valid |  | S.1.5.8.5 | Industrial Wi-Fi SYSTEM SFP Transceiver for switch | 1G SFP LC LX SMF transciever for Aruba switch | 0 | S.1.5.8.5 | FI31CE01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
108 | Valid |  | S.1.5.8.6 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | 1G SFP LC LX SMF transciever for WIFI AP | 0 | S.1.5.8.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
109 | Valid |  | S.1.5.8.7 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | Outdoor Rated FO Patch cord(5m) | 0 | S.1.5.8.7 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1 |  | Outdoor rated fiber optic patch cords (5m) to link the FPP inside the junction box to the network switch. Quantities updated: SS-070 Area: 1, SS-071 Area: 1, PKG-2 Common: 7.
110 | Valid |  | S.1.5.8.8 | Industrial Wi-Fi SYSTEM Explosion proof SFP Transceiver for switch | Outdoor Rated UTP Patch cord(5m) | 0 | S.1.5.8.8 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 16 |  | 3 |  | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 3 | 3 | [18 empty] | 1 |  | Not applicable; direct fiber connection is utilized between the FPP and the switch/IAP.
111 | Valid |  | S.1.6 | Structural Cabling System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
112 | Valid |  | S.1.6.1 | Structural Cabling System LAN outlet | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
113 | Valid |  | S.1.6.1.1 | Structural Cabling System Three(3) port Cat.6A LAN outlet / Wall mount | Three(3) port Cat.6A LAN outlet / Wall mount | 0 | S.1.6.1.1 | FI31CD02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
114 | Valid |  | S.1.6.1.2 | Structural Cabling System Two(2) port Cat.6A LAN outlet / Wall mount | Two(2) port Cat.6A LAN outlet / Wall mount | 0 | S.1.6.1.2 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 11 | [16 empty] | 4 | 7 | [17 empty] | Information outlets (duplex configuration) updated based on floor plans: PIB-080: 60 outlets, PIB-081: 11 outlets, SS-071: 11 outlets, SS-070: 9 outlets, SS-072: 7 outlets.
115 | Valid |  | S.1.6.1.3 | Structural Cabling System Floor Box with Two(2) port Cat.6A LAN outlet | Floor Box with Two(2) port Cat.6A LAN outlet | 0 | S.1.6.1.3 | FI31CD02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
116 | Valid |  | S.1.6.1.4 | Structural Cabling System Two(2) port Cat.6A LAN outlet / Ceiling mount | Two(2) port Cat.6A LAN outlet / Ceiling mount | 0 | S.1.6.1.4 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 7 | [16 empty] | 3 | 4
117 | Valid |  | S.1.6.1.5 | Structural Cabling System, Floor box with 2 receptacles | with Floor Box | 0 | S.1.6.1.5 | FI31CD01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
118 | Valid |  |  | TELECOM SYSTMEM (NON-IT) | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
119 | Valid |  | S.2 | In-Plant Voice Paging System (IVPS) | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
120 | Valid |  | S.2.1 | Paging System Main Cabinet | Main Cabinet | 0 | S.2.1 | FI32DA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 |  |  |  |  | 1 |  |  |  | Main PAGA equipment cabinet. Heat dissipation: PIB-080 main cabinet: 9265 BTUH, PIB-081 main cabinet: 4592 BTUH.
121 | Valid |  | S.2.2 | Paging System Local Cabinet | Local Cabinet | 0 | S.2.2 | FI32DB00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
122 | Valid |  | S.2.3 | Paging System PAGA Workstation with accessories | PAGA Workstation with accessories | 0 | S.2.3 | FI32DC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
123 | Valid |  | S.2.4 | Paging System Operator Access Panel | Access Control Panel | 0 | S.2.4 | FI32DD00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 10 | [26 empty] | 5 |  |  |  |  | 5 |  |  |  | Operator Access Panels installed in CCR-1 console for operator consoles: AWS4, SWS4, SRU4, and BOTB (Total: 4 panels in CCR-1).
124 | Valid |  | S.2.5 | Paging System Indoor Ceiling Speaker with Junction Box | Indoor Ceiling Speaker | 0 | S.2.5 | FI32DE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 19 | [7 empty] | 17 | [9 empty] | 2
125 | Valid |  | S.2.6 | Paging System LoudSpeaker (Box type) with Junction Box | LoudSpeaker (Box type) | 0 | S.2.6 | FI32DF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
126 | Valid |  | S.2.7 | Paging System Loudspeaker(Horn Type) with Junction Box | General Purpose | 0 | S.2.7 | FI32DG00AA-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
127 | Valid |  | S.2.8 | Paging System Loudspeaker(Horn Type) with Junction Box | Weather proof | 0 | S.2.8 | FI32DG00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 129 |  |  | 83 |  |  |  | 11 | 10 |  |  | 9 |  |  | 0 | 0 |  | 9 | 7
128 | Valid |  | S.2.9 | Paging System Loudspeaker(Horn Type) with Junction Box | Explosion Proof | 0 | S.2.9 | FI32DG00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 170 |  |  | 115 |  |  |  | 1 | 1 |  |  | 1 |  |  | 32 | 18 |  | 1 | 1
129 | Valid |  | S.2.10 | Paging System Distribution Junction Box | General Purpose | 0 | S.2.10 | FI32DJ00AA-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
130 | Valid |  | S.2.11 | Paging System Distribution Junction Box | Weather proof ( Multi JB ) | 0 | S.2.11 | FI32DJ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
131 | Valid |  | S.2.12 | Paging System Distribution Junction Box | Explosion Proof ( Multi JB ) | 0 | S.2.12 | FI32DJ00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
133 | Valid |  | S.2.14 | Paging System Intercom Station With Acoustic Booth | Intercom Station With Acoustic Booth (Ex) | 0 | S.2.14 | FI32DM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 27 |  |  | 20 | [10 empty] | 4 | 3 | [20 empty] | Acoustic booths/hoods provided for all outdoor intercom handset stations in high-noise areas (EB Complex: 17, PKG-2 Common: 8).
|  |  | S.2.14 | Paging System Intercom Station With Acoustic Booth | Intercom Station With Acoustic Booth (WP) | [7 empty] | SETS | 14 |  |  | 14
134 | Valid |  | S.2.15 | Paging System Flash Beacon | General Purpose | 0 | S.2.15 | FI32DN00AA-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
132 | Valid |  | S.2.13 | Paging System Intercom Station with Junction Box | Intercom Station with amplifier | 0 | S.2.13 | FI32DL00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 8 | [6 empty] | 2 | 2 |  |  | 2 | [5 empty] | 1 | 1
135 | Valid |  | S.2.16 | Paging System Flash Beacon | Weather proof | 0 | S.2.16 | FI32DN00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
136 | Valid |  | S.2.17 | Paging System Flash Beacon with Junction Box | Explosion Proof | 0 | S.2.17 | FI32DN00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 70 |  |  | 50 | [10 empty] | 10 | 10
137 | Valid |  | S.2.18 | Paging System Speaker Pole | Speaker Pole up to 3m | 0 | S.2.18 | FI32DO00ZZ-0000001 | 3 | 0 | 0 | BOTB-PKG1-MR-TE-0001 | SETS | 0
138 | Valid |  | S.2.19 | Paging System Speaker Pole | Speaker Pole 3m - 8m Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101 | 0 | S.2.19 | FI32DO00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 33 |  |  | 23 | [10 empty] | 5 | 5
139 | Valid |  | S.2.20 | Paging System Speaker Pole | Speaker Pole 8m - 15m | 0 | S.2.20 | FI32DO00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
140 | Valid |  | S.2.21 | Paging System Existing Interface software/license | Existing Interface software/license |  | S.2.21 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [26 empty] | 1 |  |  |  |  | 1 |  |  |  | Worst-case scenario provision: Software licenses to connect new IPVP paging system to existing call managers/servers.
|  |  | S.2.22 | Paging Remote Amplifiers | 20W, 8ohms/16ohms Indoor |  | S.2.22 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 28 | [6 empty] | 4 | 12 |  |  | 4 | [5 empty] | 4 | 4
|  |  | S.2.23 | Paging Remote Amplifiers (Weatherproof) | 20W, 8ohms/16ohms Outdoor |  | S.2.23 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 37 |  |  | 37
|  |  |  | Paging Remote Amplifiers (Explosion proof) | 20W, 8ohms/16ohms Outdoor | [7 empty] | SETS | 53 |  |  | 35 | [10 empty] | 12 | 6
|  |  | S.2.24 | Paging System Cables | 2C Unarmoured |  | S.2.24 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 1832 | [6 empty] | 220 | 340 |  |  | 972 | [5 empty] | 150 | 150
|  |  | S.2.25 | Paging System Cables | 16C Unarmoured |  | S.2.25 | FI32DP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 950 | [6 empty] | 250 | 295 |  |  | 190 | [5 empty] | 110 | 105
|  |  | S.2.26 | Paging System Cables | 2C Armoured |  | S.2.26 | FI32DP00ZZ-0000002 |  | 1 |  | BOTB-PKG1-MR-TE-0002 | M | 4136 |  |  | 3286 | [10 empty] | 592 | 258
|  |  | S.2.27 | Paging System Cables | 16C Armoured |  | S.2.27 | FI32DP00ZZ-0000003 |  | 2 |  | BOTB-PKG1-MR-TE-0003 | M | 6350 |  |  | 5300 | [10 empty] | 675 | 375
141 | Valid |  | S.3 | Emergency Siren System |  |  | S.3 | FZ75ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
142 | Valid |  | S.3.1 | Siren System Cabinet | 19" Cabinet |  | S.3.1 | FZ76ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 | [7 empty] | 2 | [9 empty] | 2
143 | Valid |  | S.3.2 | Siren System Operator Access Panel | Operator Access Panel |  | S.3.2 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [7 empty] | 1 | [9 empty] | 1
144 | Valid |  | S.3.3 | Omni-directional modularot high powered speaker array | 8 x 400W (3200W) Active Modules / 30 meters Siren Cable / Pole mount |  | S.3.3 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
145 | Valid |  | S.3.4 | Electronic Siren Controller Enclosure | Stainless steel , NEMA 4X |  | S.3.4 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
146 | Valid |  | S.3.5 | Charger, Batteries and Battery Enclosure | Stainless steel , NEMA 4X Battery & Battery Enclsure meets: SAES-T-151, SAES-P-103, 17-SAMSS-511, and IOGP S-740 |  | S.3.5 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
147 | Valid |  | S.3.6 | Flahing Beacon | Orange color |  | S.3.6 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
148 | Valid |  | S.3.7 | Flahing Beacon | Green color |  | S.3.7 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
149 | Valid |  | S.3.8 | Siren Tower | Height : 20M / Self-supporting, Ligtning protection, Maintenace Platform with ladders, Earthing and bonding Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101V |  | S.3.8 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 |  |  | 2 | [10 empty] | 1 | 1
150 | Valid |  | S.3.9 | Siren System Pole | Pole |  | S.3.9 | FZ78ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
151 | Valid |  | S.3.10 | Workstation w/monitor |  |  | S.3.10 | FZ77ZZ00ZZ-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [7 empty] | 1 | [9 empty] | 1
152 | Valid |  | S.5 | Communication System Others Telecom & Security System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
153 | Valid |  | S.5.1 | Communication System Others Telecom & Security System UPS - Cabinet Type | Telecom & Security System UPS - Cabinet Type | 0 | S.5.1 | FI37HA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
154 | Valid |  | S.5.2 | Communication System Others Patch panel | Patch panel for FIBER OPTIC | 0 | S.5.2 | FI37HB01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
155 | Valid |  | S.5.3 | Communication System Others Patch panel | Patch panel for UTP | 0 | S.5.3 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
156 | Valid |  | S.5.4 | Communication System Others Patch cord | Patch cord for Fiber OPTIC | 0 | S.5.4 | FI37HC01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
157 | Valid |  | S.5.5 | Communication System Others Patch cord | Patch cord FOR UTP | 0 | S.5.5 | FI37HC02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
158 | Valid |  | S.5.6 | Communication System Others Junction Box | Junction Box | 0 | S.5.6 | FI37HD00AA-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
159 | Valid |  | S.5.7 | Communication System Others Junction Box | Junction Box (400 x 400 x 100 ) | 0 | S.5.7 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
160 | Valid |  | S.5.8 | Communication System Others Explosion proof junction Box | Explosion proof junction Box | 0 | S.5.8 | FI37HD00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
161 | Valid |  | S.5.9 | Communication System Others Printer | FAX | 0 | S.5.9 | FI37HE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
162 | Valid |  | S.5.10 | Communication System Others Printer | Printer | 0 | S.5.10 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
163 | Valid |  | S.5.11 | Communication System Others Coax Cable | Coax Cable 1/2" | 0 | S.5.11 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 0
164 | Valid |  | S.5.12 | Communication System Others Coax Cable | Coax Cable 7/8" | 0 | S.5.12 | FI37HF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 0
165 | Valid |  | S.5.13 | Communication System Others Special Cable (Vendor Supply) | Special Cable, Wifi Antenna extension (Vendor Supply) | 0 | S.5.13 | FI37HG01ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 0
166 | Valid |  | S.5.14 | Communication System Others Special Cable (Vendor Supply) | Special Cable, Pwer Cord (Vendor Supply) | 0 | S.5.14 | FI37HG02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
167 | Valid |  | S.5.15 | Communication System Others PEDESTAL | PEDESTAL | 0 | S.5.15 | FI37HH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
168 | Valid |  | S.5.16 | Communication System Others Miscellaneous | Miscellaneous | 0 | S.5.16 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
169 | Valid |  | S.6 | IT-ACS |  |  | S.6 |  |  | 0 |  |  |  | 0
170 | Valid |  | S.6.1 | 42U Cabinet with ACS Controller |  |  | S.6.1 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1
171 | Valid |  | S.6.2 | Power Supply |  |  | S.6.2 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Rack-mount life safety power supply with battery, connected to the building UPS system for continuous operation. Quantities updated: PIB-080: 1, PIB-081: 1.
172 | Valid |  | S.6.3 | Door Contact |  |  | S.6.3 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Magnetic door contacts to monitor open/close status of single or double leaf TER doors. Quantities updated: PIB-080: 1, PIB-081: 1.
173 | Valid |  | S.6.4 | Electromagnetic Lock |  |  | S.6.4 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Electronically controlled fail-safe electromagnetic locks with secure mechanical override for TER doors. Quantities updated: PIB-080: 1, PIB-081: 1.
174 | Valid |  | S.6.5 | Card Reader with Keypad |  |  | S.6.5 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Weatherproof proximity card readers with keypads for employee ID card authorization at the TER entry door. Quantities updated: PIB-080: 1, PIB-081: 1.
175 | Valid |  | S.6.6 | Request to Exit Button |  |  | S.6.6 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Push-to-exit buttons installed on the secure side (inside) of the TER doors for standard egress. Quantities updated: PIB-080: 1, PIB-081: 1.
176 | Valid |  | S.6.7 | Emergency Break Glass |  |  | S.6.7 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 2 | [7 empty] | 1 | [9 empty] | 1 | [17 empty] | Emergency break glass units installed on the secure side (inside) of the TER doors for emergency egress. Quantities updated: PIB-080: 1, PIB-081: 1.
177 | Valid |  | S.6.8 | Indoor Dome Camera |  |  | S.6.8 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 6 | [7 empty] | 3 | [9 empty] | 3 | [17 empty] | Indoor dome cameras for TER CCTV surveillance. Exactly 3 dome cameras designated for each TER (PIB-080 TER tags PIB80-TER-IC-001/002/003, PIB-081 TER tags PIB81-TER-IC-001/002/003). Quantities updated: PIB-080: 3, PIB-081: 3.
|  |  | S.6.9 | IT-ACS Server Upgrade and Licensing (Existing) |  |  | S.6.9 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | No. | 1 | [26 empty] | 1
178 | Valid |  | S.7 | Intrusion Detection System for Category 1 Fence | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
179 | Valid |  | S.7.1 | IDAS Fixed CCTV Camera with JB and accessories | Fixed Camera with Bracket including license | 0 | S.7.1 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
180 | Valid |  | S.7.2 | IDAS PTZ CCTV Camera with JB and accessories | PTZ Camera with JB, Bracket including license | 0 | S.7.2 | FF19ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
181 | Valid |  | S.7.3 | IDAS Video Analytic Camera with JB and accessories - including license | Video Analytic Camera with Bracket including license | 0 | S.7.3 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
182 | Valid |  | S.7.4 | IDAS Camera Pole for fixed camera | Camera Pole 5m | 0 | S.7.4 | FF22ZZ00ZZ-0000001 | 5 | 0 | 0 | BOTB-PKG1-MR-TE-0001 | SETS | 0
183 | Valid |  | S.7.5 | IDAS Camera Pole for PTZ camera | Camera Pole 7m | 0 | S.7.5 | FF22ZZ00ZZ-0000001 | 7 | 0 | 0 | BOTB-PKG1-MR-TE-0001 | SETS | 0
184 | Valid |  | S.7.6 | IDAS MIDS SENSOR | Micro wave Transmitter with bracket | 0 | S.7.6 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
185 | Valid |  | S.7.7 | IDAS MIDS SENSOR | Micro wave Receiver with bracket | 0 | S.7.7 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
186 | Valid |  | S.7.8 | IDAS MIDS SENSOR | Micro wave Tranceiver with bracket | 0 | S.7.8 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
187 | Valid |  | S.7.9 | IDAS FOSS | Fiber Optic Fence Sensor Cable | 0 | S.7.9 | FR22BD00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | M | 0
188 | Valid |  | S.7.10 | IDAS FOSS | Fiber Break-out Box including all component | 0 | S.7.10 | FR21AC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
189 | Valid |  | S.7.11 | IDAS OTHERS | Magnetic Bodning Sensor | 0 | S.7.11 | FR22BC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
190 | Valid |  | S.7.12 | IDAS OTHERS | Field Equipment Cabinet including switich, APU, I/O Module, etc…and related all component. | 0 | S.7.12 | FR22BE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
191 | Valid |  | S.7.13 | IDAS OTHERS | 1G SFP LC LX SMF transciever for Juniper PE router | 0 | S.7.13 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
192 | Valid |  | S.7.14 | IDAS Camera Pole for MIDS | MIDS Pole 1.2m | 0 | S.7.14 | FF22ZZ00ZZ-0000001 | 1.2 | 0 | 0 | BOTB-PKG1-MR-TE-0001 | SETS | 0
193 | Valid |  | S.7.15 | Steel Structure Support for Field Equipment Cabinet | Steel support 1.2m x 0.8m | 0 | S.7.15 | FF22ZZ00ZZ-0000001 | 1.2 | 0 | 0 | BOTB-PKG1-MR-TE-0001 | SETS | 0
194 | Valid |  | S.7.16 | Security System Intrusion Detection System Main Cabinet | Server and FOPP 42U RACK | 0 | S.7.16 | FR22BA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
195 | Valid |  | S.7.17 | Secrutiy System Optiped for IDAS FOC Connetion | Optiped with Splicing Tray and Kit | 0 | S.7.17 | FI37HI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
196 | Valid |  | S.8 | Security CCTV & ACS System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
197 | Valid |  | S.8.1 | Security ACS Main Cabinet with ACS Controller | 42U ACS/CCTV Enclosure including switch and all related component (ACS Controller, 2 x Reader Interface Module, 2 x Ethernet Switch (POE), 2 x UTP Patch Panel, PSU, PDU, I/O Modules, RS-485 Cable) Rack Mounted UPS w/ 2-hour battery backup time | 0 | S.8.1 | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 6 | [16 empty] | 1 | 1 | [8 empty] | 1 | 1 |  | 1 | 1
198 | Valid |  | S.8.2 | Security ACS 24 Port Fiber Optic Patch Panel | 24 Port Fiber Optic Patch Panel | 0 | S.8.2 | FI37HB02ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 9 | [16 empty] | 2 | 2 | [8 empty] | 1 | 1 | [5 empty] | 3 | FOC SACS - OSP Cabinet
198 | Valid |  | S.8.3 | Security CCTV & ACS Outdoor CCTV Cabinet - | Field Equipment Cabinets (FEC) w/ Industrial Ethernet Switch (IES) with Power over Ethernet (POE), (I/O) Module, PSU, FOPP,CB, Tamper Switch | 0 | S.8.2 | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [33 empty] | 3 |  | Field Equipment Cabinets (FEC01, FEC02, FEC03) designed to withstand 65°C and house Industrial Ethernet switches, ACS controllers, I/O modules, and power supplies for the Sales Gas Scraper area. Quantities updated: PKG-2 Common: 3.
199 | Valid |  | S.8.4 | Security CCTV Indoor Fixed CCTV Camera - | Indoor Fixed CCTV Camera with Ceilling mount bracket and license | 0 | S.8.3 | FF16ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 19 | [16 empty] | 10 | 9 | [17 empty] | Indoor Fixed Dome Cameras (including ceiling mount brackets and licenses) distributed by building
200 | Valid |  | S.8.5 | Security CCTV Fixed CCTV Camera with JB and accessories - | Outdoor Fixed CCTV Camera with wall mount bracket with license | 0 | S.8.4 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 18 | [16 empty] | 10 | 8 | [17 empty] | Outdoor Fixed Cameras (including wall mount brackets, junction boxes, and licenses) distributed by building
201 | Valid |  | S.8.6 | Security ACS Proximity Card Reader | Proximity Card Reader | 0 | S.8.5 | FR21AE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [16 empty] | 7 | 7
202 | Valid |  | S.8.7 | Security ACS Electrical Magnetic Lock | Electrical Magnetic Lock | 0 | S.8.6 | FR21AH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [16 empty] | 7 | 7
203 | Valid |  | S.8.8 | Security ACS Door Contract | Door Contract | 0 | S.8.7 | FR21AI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 22 | [16 empty] | 11 | 11
204 | Valid |  | S.8.9 | Security ACS Push Button | Push Button | 0 | S.8.8 | FR21AJ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [16 empty] | 7 | 7
205 | Valid |  | S.8.10 | Security ACS Break Glass Unit | Break Glass Unit | 0 | S.8.9 | FR21AK00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [16 empty] | 7 | 7
206 | Valid |  | S.8.11 | Security CCTV & ACS Surge protector | Enclosure with Cat.6 surge protector | 0 | S.8.10 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
207 | Valid |  | S.8.12 | Tilted pole for Security CCTV | 5m, Hot-dip galvanized steel | 0 | S.8.11 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 6 | [33 empty] | 6
208 | Valid |  | S.8.13 | Tilted pole for Security CCTV | 7m, Hot-dip galvanized steel | 0 | S.8.12 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
| Valid |  | S.8.14 | CCTV Fixed CCTV Camera with JB c/w Media Converter & accessories | Explosion Proof |  | S.8.13 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 | [33 empty] | 4 |  | 2525-8540-80-R591-5973_SECURITY EQUIPMENT BLOCK AND LEVEL DIAGRAM - SALES GAS PIPELINE (FOR SCRAPPER LAUNCHER)
| Valid |  | S.8.15 | CCTV PTZ CCTV Camera with JB c/w Media Converter & accessories | Explosion Proof |  | S.8.14 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [33 empty] | 2 |  | 2525-8540-80-R591-5973_SECURITY EQUIPMENT BLOCK AND LEVEL DIAGRAM - SALES GAS PIPELINE (FOR SCRAPPER LAUNCHER)
| Valid |  | S.8.16 | Magnetic Sensor (MBS) |  |  | S.8.15 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 4 | [33 empty] | 4 |  | 2525-8540-80-R591-5973_SECURITY EQUIPMENT BLOCK AND LEVEL DIAGRAM - SALES GAS PIPELINE (FOR SCRAPPER LAUNCHER)
| Valid |  | S.8.17 | Security ACS Local Enclosure with Controller |  |  | S.8.17 | FI37HD00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [16 empty] | 7 | 7 | [16 empty] | Security ACS Local Door Controller (1 Door Capacity)
209 | Valid |  | S.10 | Process CCTV System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
210 | Valid |  | S.10.1 | CCTV Main Cabinet | Main Cabinet | 0 | S.10.1 | FF11ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 6 | [6 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 | 1 | [8 empty] | 1
211 | Valid |  | S.10.2 | CCTV Local Cabinet | Local Control Unit with Junction Box | 0 | S.10.2 | FF12ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
212 | Valid |  | S.10.3 | CCTV Outdoor CCTV Cabinet | Outdoor CCTV Cabinet | 0 | S.10.3 | FF13ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
213 | Valid |  | S.10.4 | CCTV CCTV Workstation with accessories | CCTV Workstation with accessories | 0 | S.10.4 | FF14ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [8 empty] | Worst-case scenario provision: CCTV client workstation with accessories for control room operators.
214 | Valid |  | S.10.5 | CCTV CCTV Wall Screen Monitor | CCTV Wall Screen Monitor 50" | 0 | S.10.5 | FF15ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 3 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [8 empty] | Worst-case scenario provision: Dual 24" LED monitors and 50"/75" monitors for CCTV monitoring.
214 | Valid |  | S.10.6 | CCTV CCTV Wall Screen Monitor | CCTV Wall Screen Monitor 75" | 0 | S.10.5 | FF15ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 1 | [26 empty] | 1 | [8 empty] | Worst-case scenario provision: Dual 24" LED monitors and 50"/75" monitors for CCTV monitoring.
215 | Valid |  | S.10.7 | CCTV Indoor Fixed CCTV Camera | Indoor Fixed CCTV Camera | 0 | S.10.6 | FF16ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 14 | [6 empty] | 2 | 2 |  |  | 2 | [5 empty] | 2 | 6 | [17 empty] | Process CCTV indoor fixed dome cameras for monitoring process analyzer rooms and control cabinets (PIB-080: 2, SS-071: 2).
216 | Valid |  | S.10.8 | CCTV Indoor PTZ CCTV Camera | Indoor PTZ CCTV Camera | 0 | S.10.7 | FF17ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
217 | Valid |  | S.10.9 | CCTV Fixed CCTV Camera with JB and accessories | Weather proof | 0 | S.10.8 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 20 | [6 empty] | 4 | 4 |  |  | 4 | [5 empty] | 4 | 4 | [17 empty] | Process CCTV outdoor fixed weatherproof cameras for local area surveillance (PIB-080: 4, SS-071: 4).
218 | Valid |  | S.10.10 | CCTV Fixed CCTV Camera with JB and accessories | Explosion Proof | 0 | S.10.9 | FF18ZZ00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
219 | Valid |  | S.10.11 | CCTV PTZ CCTV Camera with JB and accessories | Weather proof | 0 | S.10.10 | FF19ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
220 | Valid |  | S.10.12 | CCTV PTZ CCTV Camera with JB c/w Media Converter & accessories | Explosion Proof | 0 | S.10.11 | FF19ZZ00AD-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 28 |  |  | 2 | 3 | 3 | 1 |  |  | 6 | 1 |  |  |  | 6 | 6 | [19 empty] | Assumed QTY in PKG-2 areas | Process CCTV explosion-proof PTZ cameras for plant operational monitoring (Total: 16). Process CCTV Outdoor Junction Box (explosion-proof) housing media converters, power terminals, and fiber splicing for the 16 outdoor process cameras.
221 | Valid |  | S.10.13 | CCTV CCTV Camera Pole | IDAS Pole up to 3m | 0 | S.10.12 | FF22ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
222 | Valid |  | S.10.14 | CCTV CCTV Camera Pole | CCTV Camera Pole 3m to 8m Painting, and coating requirements: 12-SAMSS-007, SAES-H-001, and H-101V | 0 | S.10.13 | FF22ZZ00ZZ-0000001 | 5 | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 28 |  |  | 2 | 3 | 3 | 1 |  |  | 6 | 1 |  |  |  | 6 | 6 | [20 empty] | 5m tilted poles for outdoor process CCTV camera mounting (Total: 16).
223 | Valid |  | S.10.15 | CCTV Existing Interface software/license | Existing Interface software/license | 0 | S.10.14 | FF23ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 1 | [26 empty] | 1 | [8 empty] | Worst-case scenario provision: VMS expansion licenses to connect new CCTV cameras to existing corporate servers.
224 | Valid |  | S.10.16 | CCTV Server | Server | 0 | S.10.15 | FF24ZZ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 1 | [26 empty] | 1 | [8 empty] | Worst-case scenario provision: New Primary and Secondary NVRs/storage servers if existing capacity is insufficient.
227 | Valid |  | S.10.17 | Motion Sensor - Ceiling Type | Ceiling Type | 0 | S.10.18 | FH00IA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
228 | Valid |  | S.10.18 | Motion Sensor - Wall Mounting Type | Wall Mounting Type | 0 | S.10.19 | FH00IB00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
229 | Valid |  | S.10.19 | Thermal IR Camera with JB and accessories for Flare stack monitoring | Weather proof | 0 | S.10.20 | FF18ZZ00AB-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
| Valid |  | S.10.20 | Composite cable | Between JB to Camera |  | S.10.21 | FF18ZZ00AB-0000001 |  |  |  | BOTB-PKG1-MR-TE-0001 | SETS | 80 |  |  | 10 | 15 | 15 | 5 |  |  | 30 | 5 |  |  |  | 0 | 0
230 | Valid |  | S.11 | Process Access Control System | [5 empty] | 0 |  | BOTB-PKG1-MR-TE-0001 |  | 0
231 | Valid |  | S.11.1 | Access Control System Main Cabinet | Main Cabinet | 0 | 91 | FR21AA00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
232 | Valid |  | S.11.2 | Access Control System Local Cabinet | Local Cabinet | 0 | 92 | FR21AB00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
233 | Valid |  | S.11.3 | Access Control System Local Control Unit with Junction Box | Local Control Unit with Junction Box | 0 | 93 | FR21AC00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
234 | Valid |  | S.11.4 | Access Control System ACS Workstation with accessories | ACS Workstation with accessories | 0 | 94 | FR21AD00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
235 | Valid |  | S.11.5 | Access Control System Proximity Card Reader | Proximity Card Reader | 0 | 95 | FR21AE00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
236 | Valid |  | S.11.6 | Access Control System Explosion Proof Card Reader | Explosion Proof Card Reader | 0 | 96 | FR21AF00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
237 | Valid |  | S.11.7 | Access Control System Long Range Card Reader | Long Range Card Reader | 0 | 97 | FR21AG00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
238 | Valid |  | S.11.8 | Access Control System Electrical Magnetic Lock With Door Contact | Electrical Magnetic Lock With Door Contact | 0 | 98 | FR21AH00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
239 | Valid |  | S.11.9 | Access Control System Door Contract | Door Contract | 0 | 99 | FR21AI00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
240 | Valid |  | S.11.10 | Access Control System Push Button | Push Button | 0 | 100 | FR21AJ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
241 | Valid |  | S.11.11 | Access Control System Break Glass Unit | Break Glass Unit | 0 | 101 | FR21AK00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
242 | Valid |  | S.11.12 | Access Control System Turnstiles | Turnstiles | 0 | 102 | FR21AL00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
243 | Valid |  | S.11.13 | Access Control System Speed Gate | Speed Gate | 0 | 103 | FR21AM00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
244 | Valid |  | S.11.14 | Access Control System Vehicle Barrier For Gate | Vehicle Barrier For Gate | 0 | 104 | FR21AN00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
245 | Valid |  | S.11.15 | Access Control System Road Blocker | Road Blocker | 0 | 105 | FR21AO00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
246 | Valid |  | S.11.16 | Access Control System Existing Interface software/license | Existing Interface software/license | 0 | 106 | FR21AP00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 2 | [26 empty] | 1 |  |  | 1 | [5 empty] | Worst-case scenario provision: Software and reader licenses to connect the new ACS system to existing corporate servers.
247 | Valid |  | S.11.17 | Access Control System Badge Production System | Badge Production System | 0 | 107 | FR21AQ00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
248 | Valid |  | S.11.18 | Access Control System Alarm Buzzer | Alarm Buzzer | 0 | 108 | FR21AR00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
249 | Valid |  | S.11.19 | Access Control System ACS Pole | ACS Pole up to 3m | 0 | 109 | FR21AS00ZZ-0000001 |  | 0 |  | BOTB-PKG1-MR-TE-0001 | SETS | 0
250 | Valid |  | S.13 | Outside Plant Cable System |  |  | S.13 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
251 | Valid |  | S.13.1 | Fiber Optic Splice Closure | Fire-rated non-buried type |  | S.13.1 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
252 | Valid |  | S.13.2 | 144 core Fiber optic Splice Closure | Branch type (In - one 144 core cable / Out - Three 48 core cable) |  | S.13.2 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 6 |  | 2 | 2 |  |  | 2
253 | Valid |  | S.13.3 | 48 core Fiber optic Splice Closure | Branch or Butt type (In - one 48 core cable / Out - One 48 core cable) |  | S.13.3 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 6 |  | 2 | 2 |  |  | 2
254 | Valid |  | S.13.4 | 24 core Fiber optic Splice Closure | Branch or Butt type (In - one 24 core cable / Out - One 24 core cable) |  | S.13.4 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 53 |  | 9 | 27 |  |  | 9 |  |  |  |  | 4 | [15 empty] | 4
| Valid |  | S.13.5 | 6 core Fiber optic Splice Closure | Branch or Butt type (In - one 6 core cable / Out - One 6 core cable) | [8 empty] | 16 |  | 0 | 16 |  |  | 0
255 | Valid |  | S.13.6 | Telecommunication Pedestal | UPC-1278 (IT) |  | S.13.5 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 42 |  | 19 | 4 |  |  | 19
| Valid |  | S.13.7 | Telecommunication Pedestal | UPC-1278 (NON-IT) |  | S.13.6 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
256 | Valid |  | S.13.8 | Telecommunication Pedestal | UPC-1000 (IT) |  | S.13.7 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 21 |  | 9 | 3 |  |  | 9
256 | Valid |  | S.13.9 | Telecommunication Pedestal | UPC-1000 (NON-IT) |  | S.13.8 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
257 | Valid |  | S.13.10 | Telecommunication Pedestal | OPFOP1420 (IT) |  | S.13.9 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 42 |  | 10 | 22 |  |  | 10 | [29 empty] | FO PCCTV System
257 | Valid |  | S.13.11 | Telecommunication Pedestal | OPFOP1420 (NON-IT) |  | S.13.10 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 27 |  | 8 | 11 |  |  | 8
257 | Valid |  | S.13.12 | Telecommunication Pedestal | OPFOP1830 |  | S.13.11 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
257 | Valid |  | S.13.13 | Telecommunication Pedestal | CAD-8 |  | S.13.12 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 0
257 | Valid |  | S.13.14 | Telecommunication Pedestal | OPFOP1420 (SECURITY) |  | S.13.12 |  |  |  |  | BOTB-PKG2-MR-TE-0001 |  | 29 |  | 8 | 13 |  |  | 8
Note on AP12: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: Model follows the 60% FEED document
Note on V36: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on W36: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on Z36: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on AF37: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on AG37: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on V39: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on W39: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on Z39: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on AF39: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on AG39: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Company recommend to keep use 3.5kVA or less. Action: To use 3kVA
Note on V40: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on W40: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on Z40: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on AF41: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on AG41: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on V42: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on W42: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on Z42: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 apply 3kVA
Note on AF42: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on AG42: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. IFP2-PK2-CI(TE)-022 Apply 3.5kVA for SS072 and PIB-081
Note on V154: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 4 meters each to speaker
Note on W154: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 4 meters each to speaker
Note on Z154: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 4 meters each to speaker
Note on AF154: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 4 meters each to speaker
Note on AG154: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 4 meters each to speaker
Note on R156: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 7 meters each to speaker
Note on AC156: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 6 meters each to speaker
Note on AD156: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: inclkude the vertical height and termination: 6 meters each to speaker
Note on R157: HEC: +500 loop cable
Note on AC157: HEC: +175 loop cable
Note on AD157: HEC: +175 loop cable
Note on AV187: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. PRC-PK2-TQ-375 Not Required. Included in Proposal Basis document
Note on AV195: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: TQ No. PRC-PK2-TQ-375 Not Required. Included in Proposal Basis document
Note on F237: 제제헬프랑카(JEZEHEL FRANCA) 책임매니저: FSD of PCCTV
Note on Q275: HEC: data
Note on R275: HEC: data
Note on Q276: HEC: PAS
Note on R276: HEC: PAS
Note on Q277: HEC: IT:2 PAS:2 PSA:2 SACS: 2 Analyzer: 3
Note on R277: HEC: 6: PSA 4: IT 4: SACS 13: Analyzer
Note on Z277: HEC: PSA:2 PMS:2
Note on AP277: HEC: PSA:2 PMS:2
Note on R278: HEC: PCCTV

## Update Basis
Outdoor Acoustic Study
o. | Master No. | 입찰 | 수행 | 등급 | 사업영역 | 프로젝트명 | Phase | Discipline | 제목 | 적용/미적용 | 조치 계획
452 | EN-25-0275 | 필수 | 필수 | B | 화공 | Jafurah Phase II Utilities, Sulfur & Export Facilities (Package 2) for the Jafurah Gas Plant Expansion | Engineering | Control & Instrument | Aramco - Em'cy Siren System Battery 관련 요구사항 | 적용 | Emergency Siren System에 적용되는 Battery 및 Enclosure는 제조사 std.가 아닌 SAES-T-151, SAES-P-103, 17-SAMSS-511, IOGP S-740 기준에 따라 제작진행
453 | EN-25-0269 | 필수 | 필수 | B | 화공 | Jafurah Phase II Utilities, Sulfur & Export Facilities (Package 2) for the Jafurah Gas Plant Expansion | Engineering | Control & Instrument | Aramco - Telecom Pole 관련 요구사항 | 적용 | Telecom Pole 재질, Painting, Coating 관련 요구사항 확인후 MR에 반영 (12-SAMSS-007, SAES-H-001, H-101V)